## PPR PN20
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
| DIMENZIONISANJE VODOVODNE MREŽE | [8 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.0115 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Greenlife PPR PN20 DN25 | 16.6 | 0.81681 | 0.06485 | 0.084305 |  | 10 | 0.06485 | 0.084305 | 5022.3925 | 0.00018724 | 0.034319 | 100000 | 0 | 403.2677 | 403.2677 | 677.798 | 677.798 | 630.5142 | 630.5142 | 636.7167 | 636.7167 | 635.8701 | 635.8701 | 635.9851 | 635.9851 | 635.9695 | 635.9695 | 635.9716 | 635.9716 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713 | 635.9713
2-3 | 4.8 | 1 | 0.25 | Pipelife Greenlife PPR PN20 DN32 | 21.2 | 0.70824 | 0.036979 | 0.1775 |  | 10 | 0.036979 | 0.1775 | 2956.6627 | 0.00014661 | 0.023779 | 100000 | 0 | 221.441 | 221.441 | 388.6118 | 388.6118 | 359.2675 | 359.2675 | 363.1136 | 363.1136 | 362.5874 | 362.5874 | 362.659 | 362.659 | 362.6492 | 362.6492 | 362.6506 | 362.6506 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504 | 362.6504
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Greenlife PPR PN20 DN25 | 16.6 | 1.2915 | 0.14604 | 0.24826 |  | 10 | 0.14604 | 0.24826 | 12555.9814 | 0.00018724 | 0.034319 | 100000 | 0 | 1008.1694 | 1008.1694 | 1496.2361 | 1496.2361 | 1424.5818 | 1424.5818 | 1433.0825 | 1433.0825 | 1432.0459 | 1432.0459 | 1432.1719 | 1432.1719 | 1432.1566 | 1432.1566 | 1432.1585 | 1432.1585 | 1432.1582 | 1432.1582 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Greenlife PPR PN20 DN32 | 21.2 | 0.86741 | 0.052888 | 0.063466 |  | 10 | 0.052888 | 0.063466 | 4434.9941 | 0.00014661 | 0.023779 | 100000 | 0 | 332.1615 | 332.1615 | 550.5519 | 550.5519 | 514.662 | 514.662 | 519.1851 | 519.1851 | 518.5936 | 518.5936 | 518.6706 | 518.6706 | 518.6605 | 518.6605 | 518.6619 | 518.6619 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Greenlife PPR PN20 DN32 | 21.2 | 1.0624 | 0.075782 | 0.25766 |  | 10 | 0.075782 | 0.25766 | 6652.4911 | 0.00014661 | 0.023779 | 100000 | 0 | 498.2423 | 498.2423 | 782.0831 | 782.0831 | 738.5033 | 738.5033 | 743.7682 | 743.7682 | 743.1116 | 743.1116 | 743.1932 | 743.1932 | 743.183 | 743.183 | 743.1843 | 743.1843 | 743.1841 | 743.1841 | 743.1842 | 743.1842 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841 | 743.1841
6-7 | 3.4 | 5 | 0.55902 | Pipelife Greenlife PPR PN20 DN40 | 26.6 | 1.0059 | 0.051721 | 0.17585 |  | 10 | 0.051721 | 0.17585 | 4753.8219 | 0.00011685 | 0.016919 | 100000 | 0 | 334.7103 | 334.7103 | 534.4971 | 534.4971 | 503.9755 | 503.9755 | 507.6158 | 507.6158 | 507.1673 | 507.1673 | 507.2223 | 507.2223 | 507.2156 | 507.2156 | 507.2164 | 507.2164 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163 | 507.2163
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 0.76829 | 0.024085 | 0.08189 |  | 10 | 0.024085 | 0.08189 | 2208.4459 | 9.3057e-05 | 0.012025 | 100000 | 0 | 146.5124 | 146.5124 | 251.3852 | 251.3852 | 234.3471 | 234.3471 | 236.4374 | 236.4374 | 236.171 | 236.171 | 236.2048 | 236.2048 | 236.2005 | 236.2005 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201 | 236.201
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 0.90231 | 0.032057 | 0.10899 |  | 10 | 0.032057 | 0.10899 | 3046.1323 | 9.3057e-05 | 0.012025 | 100000 | 0 | 202.0861 | 202.0861 | 332.3694 | 332.3694 | 312.2415 | 312.2415 | 314.6366 | 314.6366 | 314.3416 | 314.3416 | 314.3778 | 314.3778 | 314.3733 | 314.3733 | 314.3739 | 314.3739 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 0.99868 | 0.038417 | 0.13062 |  | 10 | 0.038417 | 0.13062 | 3731.512 | 9.3057e-05 | 0.012025 | 100000 | 0 | 247.5554 | 247.5554 | 396.7332 | 396.7332 | 374.4216 | 374.4216 | 377.0233 | 377.0233 | 376.7101 | 376.7101 | 376.7476 | 376.7476 | 376.7431 | 376.7431 | 376.7437 | 376.7437 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN20 DN75 | 50 | 0.49312 | 0.00663 | 0.022542 |  | 10 | 0.00663 | 0.022542 | 607.7463 | 6.2162e-05 | 0.0065652 | 100000 | 0 | 36.4855 | 36.4855 | 70.328 | 70.328 | 64.3516 | 64.3516 | 65.1077 | 65.1077 | 65.0073 | 65.0073 | 65.0206 | 65.0206 | 65.0188 | 65.0188 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019 | 65.019
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 1.1851 | 0.052182 | 0.17742 |  | 10 | 0.052182 | 0.17742 | 5254.5781 | 9.3057e-05 | 0.012025 | 100000 | 0 | 348.5985 | 348.5985 | 535.5058 | 535.5058 | 509.0756 | 509.0756 | 512.0483 | 512.0483 | 511.7045 | 511.7045 | 511.7441 | 511.7441 | 511.7395 | 511.7395 | 511.7401 | 511.7401 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.80699 | 0.019747 | 0.067138 |  | 10 | 0.019747 | 0.067138 | 1937.6023 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 121.3542 | 121.3542 | 205.3761 | 205.3761 | 192.2662 | 192.2662 | 193.8215 | 193.8215 | 193.6302 | 193.6302 | 193.6536 | 193.6536 | 193.6508 | 193.6508 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.85117 | 0.021715 | 0.086861 |  | 10 | 0.021715 | 0.086861 | 2155.5825 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 135.0065 | 135.0065 | 225.3767 | 225.3767 | 211.5041 | 211.5041 | 213.1336 | 213.1336 | 212.9355 | 212.9355 | 212.9595 | 212.9595 | 212.9566 | 212.9566 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.88401 | 0.023233 | 0.037173 |  | 10 | 0.023233 | 0.037173 | 2325.1227 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 145.625 | 145.625 | 240.776 | 240.776 | 226.3387 | 226.3387 | 228.0224 | 228.0224 | 227.8193 | 227.8193 | 227.8437 | 227.8437 | 227.8408 | 227.8408 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 0.90231 | 0.032057 | 0.10899 |  | 10 | 0.032057 | 0.10899 | 3046.1323 | 9.3057e-05 | 0.012025 | 100000 | 0 | 202.0861 | 202.0861 | 332.3694 | 332.3694 | 312.2415 | 312.2415 | 314.6366 | 314.6366 | 314.3416 | 314.3416 | 314.3778 | 314.3778 | 314.3733 | 314.3733 | 314.3739 | 314.3739 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738 | 314.3738
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 0.99868 | 0.038417 | 0.13062 |  | 10 | 0.038417 | 0.13062 | 3731.512 | 9.3057e-05 | 0.012025 | 100000 | 0 | 247.5554 | 247.5554 | 396.7332 | 396.7332 | 374.4216 | 374.4216 | 377.0233 | 377.0233 | 376.7101 | 376.7101 | 376.7476 | 376.7476 | 376.7431 | 376.7431 | 376.7437 | 376.7437 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436 | 376.7436
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 1.1051 | 0.046041 | 0.15654 |  | 10 | 0.046041 | 0.15654 | 4569.1984 | 9.3057e-05 | 0.012025 | 100000 | 0 | 303.1291 | 303.1291 | 473.6774 | 473.6774 | 448.9964 | 448.9964 | 451.8144 | 451.8144 | 451.483 | 451.483 | 451.5219 | 451.5219 | 451.5173 | 451.5173 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178 | 451.5178
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN20 DN50 | 33.4 | 1.1851 | 0.052182 | 0.17742 |  | 10 | 0.052182 | 0.17742 | 5254.5781 | 9.3057e-05 | 0.012025 | 100000 | 0 | 348.5985 | 348.5985 | 535.5058 | 535.5058 | 509.0756 | 509.0756 | 512.0483 | 512.0483 | 511.7045 | 511.7045 | 511.7441 | 511.7441 | 511.7395 | 511.7395 | 511.7401 | 511.7401 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74 | 511.74
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.80699 | 0.019747 | 0.067138 |  | 10 | 0.019747 | 0.067138 | 1937.6023 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 121.3542 | 121.3542 | 205.3761 | 205.3761 | 192.2662 | 192.2662 | 193.8215 | 193.8215 | 193.6302 | 193.6302 | 193.6536 | 193.6536 | 193.6508 | 193.6508 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.85117 | 0.021715 | 0.086861 |  | 10 | 0.021715 | 0.086861 | 2155.5825 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 135.0065 | 135.0065 | 225.3767 | 225.3767 | 211.5041 | 211.5041 | 213.1336 | 213.1336 | 212.9355 | 212.9355 | 212.9595 | 212.9595 | 212.9566 | 212.9566 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569 | 212.9569
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.88401 | 0.023233 | 0.037173 |  | 10 | 0.023233 | 0.037173 | 2325.1227 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 145.625 | 145.625 | 240.776 | 240.776 | 226.3387 | 226.3387 | 228.0224 | 228.0224 | 227.8193 | 227.8193 | 227.8437 | 227.8437 | 227.8408 | 227.8408 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN20 DN63 | 42 | 0.88401 | 0.023233 | 0.037173 |  | 10 | 0.023233 | 0.037173 | 2325.1227 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 145.625 | 145.625 | 240.776 | 240.776 | 226.3387 | 226.3387 | 228.0224 | 228.0224 | 227.8193 | 227.8193 | 227.8437 | 227.8437 | 227.8408 | 227.8408 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411 | 227.8411
[7 empty] | SH = | 1.7197 | m

## PPR GFR
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
DIMENZIONISANJE VODOVODNE MREŽE | [9 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.01 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 1.0855 | 0.12768 | 0.16598 |  | 10 | 0.12768 | 0.16598 | 10224.4189 | 0.00018769 | 0.042477 | 100000 | 0 | 838.4144 | 838.4144 | 1321.7448 | 1321.7448 | 1243.2705 | 1243.2705 | 1253.2807 | 1253.2807 | 1251.9599 | 1251.9599 | 1252.1334 | 1252.1334 | 1252.1106 | 1252.1106 | 1252.1136 | 1252.1136 | 1252.1132 | 1252.1132 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133
2-3 | 4.8 | 1 | 0.25 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 1.5351 | 0.2363 | 1.1342 |  | 10 | 0.2363 | 1.1342 | 20448.8377 | 0.00018769 | 0.042477 | 100000 | 0 | 1676.8287 | 1676.8287 | 2411.7237 | 2411.7237 | 2306.2235 | 2306.2235 | 2318.661 | 2318.661 | 2317.1575 | 2317.1575 | 2317.3387 | 2317.3387 | 2317.3169 | 2317.3169 | 2317.3195 | 2317.3195 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 1.7162 | 0.28846 | 0.49038 |  | 10 | 0.28846 | 0.49038 | 25561.0472 | 0.00018769 | 0.042477 | 100000 | 0 | 2096.0359 | 2096.0359 | 2932.1727 | 2932.1727 | 2817.0189 | 2817.0189 | 2830.2208 | 2830.2208 | 2828.6727 | 2828.6727 | 2828.8538 | 2828.8538 | 2828.8326 | 2828.8326 | 2828.8351 | 2828.8351 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348 | 2828.8348
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 1.8801 | 0.33967 | 0.40761 |  | 10 | 0.33967 | 0.40761 | 30673.2566 | 0.00018769 | 0.042477 | 100000 | 0 | 2515.2431 | 2515.2431 | 3442.0097 | 3442.0097 | 3318.7292 | 3318.7292 | 3332.5298 | 3332.5298 | 3330.9527 | 3330.9527 | 3331.1325 | 3331.1325 | 3331.112 | 3331.112 | 3331.1144 | 3331.1144 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141 | 3331.1141
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Greenlife PPR GFR PN16 DN40 | 29 | 0.56773 | 0.016808 | 0.057147 |  | 10 | 0.016808 | 0.057147 | 1388.9084 | 9.3197e-05 | 0.014863 | 100000 | 0 | 93.5442 | 93.5442 | 178.7064 | 178.7064 | 163.0059 | 163.0059 | 165.087 | 165.087 | 164.7971 | 164.7971 | 164.8372 | 164.8372 | 164.8316 | 164.8316 | 164.8324 | 164.8324 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323 | 164.8323
6-7 | 3.4 | 5 | 0.55902 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 3.4325 | 1.0108 | 3.4367 |  | 10 | 1.0108 | 3.4367 | 102244.1887 | 0.00018769 | 0.042477 | 100000 | 0 | 8384.1435 | 8384.1435 | 10072.5759 | 10072.5759 | 9897.9294 | 9897.9294 | 9914.1777 | 9914.1777 | 9912.6504 | 9912.6504 | 9912.7938 | 9912.7938 | 9912.7804 | 9912.7804 | 9912.7816 | 9912.7816 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815 | 9912.7815
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 4.1333 | 1.4211 | 4.8316 |  | 10 | 1.4211 | 4.8316 | 148254.0736 | 0.00018769 | 0.042477 | 100000 | 0 | 12157.0081 | 12157.0081 | 14106.1914 | 14106.1914 | 13921.3895 | 13921.3895 | 13937.4449 | 13937.4449 | 13936.039 | 13936.039 | 13936.1621 | 13936.1621 | 13936.1513 | 13936.1513 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522 | 13936.1522
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR GFR PN16 DN125 | 90.8 | 0.12209 | 0.00027141 | 0.00092278 |  | 10 | 0.00027141 | 0.00092278 | 20.5141 | 2.9765e-05 | 0.0026827 | 100000 | 0 | 1.0513 | 1.0513 | 3.0881 | 3.0881 | 2.6019 | 2.6019 | 2.6709 | 2.6709 | 2.6602 | 2.6602 | 2.6618 | 2.6618 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 5.3727 | 2.3066 | 7.8423 |  | 10 | 2.3066 | 7.8423 | 250498.2623 | 0.00018769 | 0.042477 | 100000 | 0 | 20541.1516 | 20541.1516 | 22793.58 | 22793.58 | 22606.4364 | 22606.4364 | 22621.041 | 22621.041 | 22619.8955 | 22619.8955 | 22619.9853 | 22619.9853 | 22619.9783 | 22619.9783 | 22619.9789 | 22619.9789 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 5.9453 | 2.7839 | 9.4654 |  | 10 | 2.7839 | 9.4654 | 306732.566 | 0.00018769 | 0.042477 | 100000 | 0 | 25152.4306 | 25152.4306 | 27471.33 | 27471.33 | 27288.7939 | 27288.7939 | 27302.4124 | 27302.4124 | 27301.3922 | 27301.3922 | 27301.4686 | 27301.4686 | 27301.4629 | 27301.4629 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633 | 27301.4633
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR GFR PN16 DN110 | 79.8 | 0.20761 | 0.00080523 | 0.0027378 |  | 10 | 0.00080523 | 0.0027378 | 67.4925 | 3.3868e-05 | 0.0032561 | 100000 | 0 | 3.5587 | 3.5587 | 8.8954 | 8.8954 | 7.7628 | 7.7628 | 7.9162 | 7.9162 | 7.8939 | 7.8939 | 7.8971 | 7.8971 | 7.8966 | 7.8966 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 6.865 | 3.6405 | 12.3777 |  | 10 | 3.6405 | 12.3777 | 408976.7547 | 0.00018769 | 0.042477 | 100000 | 0 | 33536.5741 | 33536.5741 | 35859.5511 | 35859.5511 | 35690.7166 | 35690.7166 | 35702.4912 | 35702.4912 | 35701.6677 | 35701.6677 | 35701.7253 | 35701.7253 | 35701.7212 | 35701.7212 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 7.2409 | 4.0223 | 16.0891 |  | 10 | 4.0223 | 16.0891 | 454986.6396 | 0.00018769 | 0.042477 | 100000 | 0 | 37309.4387 | 37309.4387 | 39596.7138 | 39596.7138 | 39435.4682 | 39435.4682 | 39446.424 | 39446.424 | 39445.6777 | 39445.6777 | 39445.7285 | 39445.7285 | 39445.7251 | 39445.7251 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 7.5202 | 4.3179 | 6.9087 |  | 10 | 4.3179 | 6.9087 | 490772.1057 | 0.00018769 | 0.042477 | 100000 | 0 | 40243.8889 | 40243.8889 | 42490.3425 | 42490.3425 | 42335.4163 | 42335.4163 | 42345.7458 | 42345.7458 | 42345.0555 | 42345.0555 | 42345.1017 | 42345.1017 | 42345.0986 | 42345.0986 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR GFR PN16 DN125 | 90.8 | 0.12209 | 0.00027141 | 0.00092278 |  | 10 | 0.00027141 | 0.00092278 | 20.5141 | 2.9765e-05 | 0.0026827 | 100000 | 0 | 1.0513 | 1.0513 | 3.0881 | 3.0881 | 2.6019 | 2.6019 | 2.6709 | 2.6709 | 2.6602 | 2.6602 | 2.6618 | 2.6618 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616 | 2.6616
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 5.3727 | 2.3066 | 7.8423 |  | 10 | 2.3066 | 7.8423 | 250498.2623 | 0.00018769 | 0.042477 | 100000 | 0 | 20541.1516 | 20541.1516 | 22793.58 | 22793.58 | 22606.4364 | 22606.4364 | 22621.041 | 22621.041 | 22619.8955 | 22619.8955 | 22619.9853 | 22619.9853 | 22619.9783 | 22619.9783 | 22619.9789 | 22619.9789 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788 | 22619.9788
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR GFR PN16 DN50 | 36.2 | 0.94076 | 0.031111 | 0.10578 |  | 10 | 0.031111 | 0.10578 | 3055.1286 | 7.466e-05 | 0.010657 | 100000 | 0 | 194.319 | 194.319 | 322.8599 | 322.8599 | 302.9976 | 302.9976 | 305.3524 | 305.3524 | 305.0634 | 305.0634 | 305.0987 | 305.0987 | 305.0944 | 305.0944 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949 | 305.0949
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR GFR PN16 DN110 | 79.8 | 0.20761 | 0.00080523 | 0.0027378 |  | 10 | 0.00080523 | 0.0027378 | 67.4925 | 3.3868e-05 | 0.0032561 | 100000 | 0 | 3.5587 | 3.5587 | 8.8954 | 8.8954 | 7.7628 | 7.7628 | 7.9162 | 7.9162 | 7.8939 | 7.8939 | 7.8971 | 7.8971 | 7.8966 | 7.8966 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967 | 7.8967
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 6.865 | 3.6405 | 12.3777 |  | 10 | 3.6405 | 12.3777 | 408976.7547 | 0.00018769 | 0.042477 | 100000 | 0 | 33536.5741 | 33536.5741 | 35859.5511 | 35859.5511 | 35690.7166 | 35690.7166 | 35702.4912 | 35702.4912 | 35701.6677 | 35701.6677 | 35701.7253 | 35701.7253 | 35701.7212 | 35701.7212 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215 | 35701.7215
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 7.2409 | 4.0223 | 16.0891 |  | 10 | 4.0223 | 16.0891 | 454986.6396 | 0.00018769 | 0.042477 | 100000 | 0 | 37309.4387 | 37309.4387 | 39596.7138 | 39596.7138 | 39435.4682 | 39435.4682 | 39446.424 | 39446.424 | 39445.6777 | 39445.6777 | 39445.7285 | 39445.7285 | 39445.7251 | 39445.7251 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253 | 39445.7253
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 7.5202 | 4.3179 | 6.9087 |  | 10 | 4.3179 | 6.9087 | 490772.1057 | 0.00018769 | 0.042477 | 100000 | 0 | 40243.8889 | 40243.8889 | 42490.3425 | 42490.3425 | 42335.4163 | 42335.4163 | 42345.7458 | 42345.7458 | 42345.0555 | 42345.0555 | 42345.1017 | 42345.1017 | 42345.0986 | 42345.0986 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 7.5202 | 4.3179 | 6.9087 |  | 10 | 4.3179 | 6.9087 | 490772.1057 | 0.00018769 | 0.042477 | 100000 | 0 | 40243.8889 | 40243.8889 | 42490.3425 | 42490.3425 | 42335.4163 | 42335.4163 | 42345.7458 | 42345.7458 | 42345.0555 | 42345.0555 | 42345.1017 | 42345.1017 | 42345.0986 | 42345.0986 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988 | 42345.0988
[7 empty] | SH = | 63.2106 | m

## RADOPRESS
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
DIMENZIONISANJE VODOVODNE MREŽE | [9 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.01 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Radopress PN10 DN16 | 12 | 1.563 | 0.30726 | 0.39944 |  | 10 | 0.30726 | 0.39944 | 25441.626 | 0.00022523 | 0.055838 | 100000 | 0 | 2206.034 | 2206.034 | 3133.2739 | 3133.2739 | 2998.93 | 2998.93 | 3015.0128 | 3015.0128 | 3013.0396 | 3013.0396 | 3013.2809 | 3013.2809 | 3013.2514 | 3013.2514 | 3013.255 | 3013.255 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546 | 3013.2546
2-3 | 4.8 | 1 | 0.25 | Pipelife Radopress PN10 DN16 | 12 | 2.2105 | 0.57163 | 2.7438 |  | 10 | 0.57163 | 2.7438 | 50883.2519 | 0.00022523 | 0.055838 | 100000 | 0 | 4412.0679 | 4412.0679 | 5759.569 | 5759.569 | 5589.1071 | 5589.1071 | 5607.6901 | 5607.6901 | 5605.6292 | 5605.6292 | 5605.8573 | 5605.8573 | 5605.8321 | 5605.8321 | 5605.8349 | 5605.8349 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346 | 5605.8346
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Radopress PN10 DN16 | 12 | 2.4714 | 0.69906 | 1.1884 |  | 10 | 0.69906 | 1.1884 | 63604.0649 | 0.00022523 | 0.055838 | 100000 | 0 | 5515.0849 | 5515.0849 | 7019.9844 | 7019.9844 | 6838.2167 | 6838.2167 | 6857.3817 | 6857.3817 | 6855.3303 | 6855.3303 | 6855.5495 | 6855.5495 | 6855.5261 | 6855.5261 | 6855.5286 | 6855.5286 | 6855.5283 | 6855.5283 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284 | 6855.5284
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Radopress PN10 DN16 | 12 | 2.7073 | 0.82442 | 0.98931 |  | 10 | 0.82442 | 0.98931 | 76324.8779 | 0.00022523 | 0.055838 | 100000 | 0 | 6618.1019 | 6618.1019 | 8257.783 | 8257.783 | 8067.2835 | 8067.2835 | 8086.8033 | 8086.8033 | 8084.776 | 8084.776 | 8084.9862 | 8084.9862 | 8084.9644 | 8084.9644 | 8084.9667 | 8084.9667 | 8084.9664 | 8084.9664 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665 | 8084.9665
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Radopress PN10 DN20 | 16 | 1.8651 | 0.29335 | 0.99739 |  | 10 | 0.29335 | 0.99739 | 27168.3769 | 0.00016892 | 0.036268 | 100000 | 0 | 2159.098 | 2159.098 | 2973.8701 | 2973.8701 | 2866.0785 | 2866.0785 | 2878.0407 | 2878.0407 | 2876.6852 | 2876.6852 | 2876.8385 | 2876.8385 | 2876.8211 | 2876.8211 | 2876.8231 | 2876.8231 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229 | 2876.8229
6-7 | 3.4 | 5 | 0.55902 | Pipelife Radopress PN10 DN16 | 12 | 4.9428 | 2.4803 | 8.4329 |  | 10 | 2.4803 | 8.4329 | 254416.2596 | 0.00022523 | 0.055838 | 100000 | 0 | 22060.3395 | 22060.3395 | 24522.3825 | 24522.3825 | 24307.216 | 24307.216 | 24324.8651 | 24324.8651 | 24323.4097 | 24323.4097 | 24323.5296 | 24323.5296 | 24323.5197 | 24323.5197 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205 | 24323.5205
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Radopress PN10 DN33 | 26 | 1.2679 | 0.080039 | 0.27213 |  | 10 | 0.080039 | 0.27213 | 7725.9582 | 0.00010395 | 0.017508 | 100000 | 0 | 535.6754 | 535.6754 | 822.2601 | 822.2601 | 780.6194 | 780.6194 | 785.4361 | 785.4361 | 784.8627 | 784.8627 | 784.9307 | 784.9307 | 784.9227 | 784.9227 | 784.9236 | 784.9236 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235 | 784.9235
8-9 | 3.4 | 10 | 0.79057 | Pipelife Radopress PN10 DN16 | 12 | 6.9902 | 4.7228 | 16.0575 |  | 10 | 4.7228 | 16.0575 | 508832.5191 | 0.00022523 | 0.055838 | 100000 | 0 | 44120.679 | 44120.679 | 46474.6617 | 46474.6617 | 46304.5126 | 46304.5126 | 46316.4215 | 46316.4215 | 46315.5861 | 46315.5861 | 46315.6447 | 46315.6447 | 46315.6406 | 46315.6406 | 46315.6409 | 46315.6409 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Radopress PN10 DN26 | 20 | 2.7852 | 0.45876 | 1.5598 |  | 10 | 0.45876 | 1.5598 | 48469.3504 | 0.00013514 | 0.025951 | 100000 | 0 | 3612.1027 | 3612.1027 | 4598.7959 | 4598.7959 | 4489.2944 | 4489.2944 | 4499.8973 | 4499.8973 | 4498.8563 | 4498.8563 | 4498.9584 | 4498.9584 | 4498.9484 | 4498.9484 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493
10-11 | 3.4 | 15 | 0.96825 | Pipelife Radopress PN10 DN42 | 33 | 1.1321 | 0.048573 | 0.16515 |  | 10 | 0.048573 | 0.16515 | 4852.9146 | 8.19e-05 | 0.012244 | 100000 | 0 | 316.042 | 316.042 | 500.7302 | 500.7302 | 473.5341 | 473.5341 | 476.6756 | 476.6756 | 476.3014 | 476.3014 | 476.3458 | 476.3458 | 476.3406 | 476.3406 | 476.3412 | 476.3412 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411 | 476.3411
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Radopress PN10 DN33 | 26 | 1.9557 | 0.17445 | 0.59312 |  | 10 | 0.17445 | 0.59312 | 18382.4523 | 0.00010395 | 0.017508 | 100000 | 0 | 1274.5381 | 1274.5381 | 1766.4016 | 1766.4016 | 1704.9624 | 1704.9624 | 1711.3807 | 1711.3807 | 1710.6967 | 1710.6967 | 1710.7694 | 1710.7694 | 1710.7617 | 1710.7617 | 1710.7625 | 1710.7625 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624 | 1710.7624
12-13 | 3.4 | 20 | 1.118 | Pipelife Radopress PN10 DN16 | 12 | 9.8856 | 9.0591 | 30.801 |  | 10 | 9.0591 | 30.801 | 1017665.0383 | 0.00022523 | 0.055838 | 100000 | 0 | 88241.3581 | 88241.3581 | 88876.0275 | 88876.0275 | 88838.8866 | 88838.8866 | 88841.0501 | 88841.0501 | 88840.9241 | 88840.9241 | 88840.9314 | 88840.9314 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931
13-14 | 4 | 22.25 | 1.1792 | Pipelife Radopress PN10 DN63 | 54 | 0.51491 | 0.0064852 | 0.025941 |  | 10 | 0.0064852 | 0.025941 | 613.5392 | 5.005e-05 | 0.0058494 | 100000 | 0 | 35.385 | 35.385 | 68.8239 | 68.8239 | 62.9482 | 62.9482 | 63.6853 | 63.6853 | 63.5883 | 63.5883 | 63.601 | 63.601 | 63.5993 | 63.5993 | 63.5996 | 63.5996 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995
14-15 | 1.6 | 24 | 1.2247 | Pipelife Radopress PN10 DN16 | 12 | 10.8291 | 10.765 | 17.224 |  | 10 | 10.765 | 17.224 | 1221198.0459 | 0.00022523 | 0.055838 | 100000 | 0 | 105889.6297 | 105889.6297 | 105552.6048 | 105552.6048 | 105571.1939 | 105571.1939 | 105570.1665 | 105570.1665 | 105570.2233 | 105570.2233 | 105570.2201 | 105570.2201 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203
8-9 | 3.4 | 10 | 0.79057 | Pipelife Radopress PN10 DN16 | 12 | 6.9902 | 4.7228 | 16.0575 |  | 10 | 4.7228 | 16.0575 | 508832.5191 | 0.00022523 | 0.055838 | 100000 | 0 | 44120.679 | 44120.679 | 46474.6617 | 46474.6617 | 46304.5126 | 46304.5126 | 46316.4215 | 46316.4215 | 46315.5861 | 46315.5861 | 46315.6447 | 46315.6447 | 46315.6406 | 46315.6406 | 46315.6409 | 46315.6409 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408 | 46315.6408
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Radopress PN10 DN26 | 20 | 2.7852 | 0.45876 | 1.5598 |  | 10 | 0.45876 | 1.5598 | 48469.3504 | 0.00013514 | 0.025951 | 100000 | 0 | 3612.1027 | 3612.1027 | 4598.7959 | 4598.7959 | 4489.2944 | 4489.2944 | 4499.8973 | 4499.8973 | 4498.8563 | 4498.8563 | 4498.9584 | 4498.9584 | 4498.9484 | 4498.9484 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493 | 4498.9493
10-11 | 3.4 | 15 | 0.96825 | Pipelife Radopress PN10 DN16 | 12 | 8.5612 | 6.9071 | 23.4841 |  | 10 | 6.9071 | 23.4841 | 763248.7787 | 0.00022523 | 0.055838 | 100000 | 0 | 66181.0186 | 66181.0186 | 67836.0958 | 67836.0958 | 67730.0864 | 67730.0864 | 67736.7713 | 67736.7713 | 67736.3493 | 67736.3493 | 67736.376 | 67736.376 | 67736.3743 | 67736.3743 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744 | 67736.3744
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Radopress PN10 DN16 | 12 | 9.1808 | 7.8787 | 26.7875 |  | 10 | 7.8787 | 26.7875 | 877736.0955 | 0.00022523 | 0.055838 | 100000 | 0 | 76108.1713 | 76108.1713 | 77335.4704 | 77335.4704 | 77260.1994 | 77260.1994 | 77264.7691 | 77264.7691 | 77264.4915 | 77264.4915 | 77264.5083 | 77264.5083 | 77264.5073 | 77264.5073 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074 | 77264.5074
12-13 | 3.4 | 20 | 1.118 | Pipelife Radopress PN10 DN16 | 12 | 9.8856 | 9.0591 | 30.801 |  | 10 | 9.0591 | 30.801 | 1017665.0383 | 0.00022523 | 0.055838 | 100000 | 0 | 88241.3581 | 88241.3581 | 88876.0275 | 88876.0275 | 88838.8866 | 88838.8866 | 88841.0501 | 88841.0501 | 88840.9241 | 88840.9241 | 88840.9314 | 88840.9314 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931 | 88840.931
13-14 | 4 | 22.25 | 1.1792 | Pipelife Radopress PN10 DN63 | 54 | 0.51491 | 0.0064852 | 0.025941 |  | 10 | 0.0064852 | 0.025941 | 613.5392 | 5.005e-05 | 0.0058494 | 100000 | 0 | 35.385 | 35.385 | 68.8239 | 68.8239 | 62.9482 | 62.9482 | 63.6853 | 63.6853 | 63.5883 | 63.5883 | 63.601 | 63.601 | 63.5993 | 63.5993 | 63.5996 | 63.5996 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995 | 63.5995
14-15 | 1.6 | 24 | 1.2247 | Pipelife Radopress PN10 DN16 | 12 | 10.8291 | 10.765 | 17.224 |  | 10 | 10.765 | 17.224 | 1221198.0459 | 0.00022523 | 0.055838 | 100000 | 0 | 105889.6297 | 105889.6297 | 105552.6048 | 105552.6048 | 105571.1939 | 105571.1939 | 105570.1665 | 105570.1665 | 105570.2233 | 105570.2233 | 105570.2201 | 105570.2201 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203
14-15 | 1.6 | 24 | 1.2247 | Pipelife Radopress PN10 DN16 | 12 | 10.8291 | 10.765 | 17.224 |  | 10 | 10.765 | 17.224 | 1221198.0459 | 0.00022523 | 0.055838 | 100000 | 0 | 105889.6297 | 105889.6297 | 105552.6048 | 105552.6048 | 105571.1939 | 105571.1939 | 105570.1665 | 105570.1665 | 105570.2233 | 105570.2233 | 105570.2201 | 105570.2201 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203 | 105570.2203
[7 empty] | SH = | 81.4499 | m

## PPR PN16
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
DIMENZIONISANJE VODOVODNE MREŽE | [9 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.01 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Greenlife PPR PN16 DN20 | 14.4 | 1.0855 | 0.12768 | 0.16598 |  | 10 | 0.12768 | 0.16598 | 10224.4189 | 0.00018769 | 0.042477 | 100000 | 0 | 838.4144 | 838.4144 | 1321.7448 | 1321.7448 | 1243.2705 | 1243.2705 | 1253.2807 | 1253.2807 | 1251.9599 | 1251.9599 | 1252.1334 | 1252.1334 | 1252.1106 | 1252.1106 | 1252.1136 | 1252.1136 | 1252.1132 | 1252.1132 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133 | 1252.1133
2-3 | 4.8 | 1 | 0.25 | Pipelife Greenlife PPR PN16 DN20 | 14.4 | 1.5351 | 0.2363 | 1.1342 |  | 10 | 0.2363 | 1.1342 | 20448.8377 | 0.00018769 | 0.042477 | 100000 | 0 | 1676.8287 | 1676.8287 | 2411.7237 | 2411.7237 | 2306.2235 | 2306.2235 | 2318.661 | 2318.661 | 2317.1575 | 2317.1575 | 2317.3387 | 2317.3387 | 2317.3169 | 2317.3169 | 2317.3195 | 2317.3195 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192 | 2317.3192
3-4 | 1.7 | 2 | 0.35355 | Pipelife Greenlife PPR PN16 DN20 | 14.4 | 2.1709 | 0.44 | 0.74799 |  | 10 | 0.44 | 0.74799 | 40897.6755 | 0.00018769 | 0.042477 | 100000 | 0 | 3353.6574 | 3353.6574 | 4438.0725 | 4438.0725 | 4301.73 | 4301.73 | 4316.3996 | 4316.3996 | 4314.7929 | 4314.7929 | 4314.9685 | 4314.9685 | 4314.9493 | 4314.9493 | 4314.9514 | 4314.9514 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512 | 4314.9512
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 2.8972 | 0.97286 | 1.1674 |  | 10 | 0.97286 | 1.1674 | 90423.7267 | 0.00023299 | 0.058751 | 100000 | 0 | 7924.2666 | 7924.2666 | 9725.7314 | 9725.7314 | 9522.1097 | 9522.1097 | 9542.5844 | 9542.5844 | 9540.5002 | 9540.5002 | 9540.7121 | 9540.7121 | 9540.6905 | 9540.6905 | 9540.6927 | 9540.6927 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925 | 9540.6925
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Greenlife PPR PN16 DN25 | 18 | 1.4737 | 0.16591 | 0.56411 |  | 10 | 0.16591 | 0.56411 | 15076.5191 | 0.00015015 | 0.030394 | 100000 | 0 | 1157.7759 | 1157.7759 | 1695.9737 | 1695.9737 | 1619.112 | 1619.112 | 1628.0468 | 1628.0468 | 1626.981 | 1626.981 | 1627.1077 | 1627.1077 | 1627.0927 | 1627.0927 | 1627.0945 | 1627.0945 | 1627.0942 | 1627.0942 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943 | 1627.0943
6-7 | 3.4 | 5 | 0.55902 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 5.2896 | 2.9332 | 9.9729 |  | 10 | 2.9332 | 9.9729 | 301412.4225 | 0.00023299 | 0.058751 | 100000 | 0 | 26414.2218 | 26414.2218 | 28964.7406 | 28964.7406 | 28749.3614 | 28749.3614 | 28766.5652 | 28766.5652 | 28765.1848 | 28765.1848 | 28765.2955 | 28765.2955 | 28765.2866 | 28765.2866 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873 | 28765.2873
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Greenlife PPR PN16 DN32 | 23.2 | 1.5924 | 0.13878 | 0.47187 |  | 10 | 0.13878 | 0.47187 | 13657.7504 | 0.0001165 | 0.020772 | 100000 | 0 | 976.6816 | 976.6816 | 1414.5616 | 1414.5616 | 1355.0908 | 1355.0908 | 1361.7022 | 1361.7022 | 1360.9494 | 1360.9494 | 1361.0348 | 1361.0348 | 1361.0251 | 1361.0251 | 1361.0262 | 1361.0262 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261 | 1361.0261
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 7.4806 | 5.5927 | 19.0152 |  | 10 | 5.5927 | 19.0152 | 602824.8449 | 0.00023299 | 0.058751 | 100000 | 0 | 52828.4437 | 52828.4437 | 54987.1716 | 54987.1716 | 54837.0855 | 54837.0855 | 54847.2628 | 54847.2628 | 54846.5715 | 54846.5715 | 54846.6185 | 54846.6185 | 54846.6153 | 54846.6153 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN16 DN40 | 29 | 1.3247 | 0.075566 | 0.25692 |  | 10 | 0.075566 | 0.25692 | 7561.8349 | 9.3197e-05 | 0.014863 | 100000 | 0 | 509.2963 | 509.2963 | 774.8766 | 774.8766 | 737.243 | 737.243 | 741.5068 | 741.5068 | 741.0102 | 741.0102 | 741.0679 | 741.0679 | 741.0612 | 741.0612 | 741.062 | 741.062 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 9.1618 | 8.1858 | 27.8316 |  | 10 | 8.1858 | 27.8316 | 904237.2674 | 0.00023299 | 0.058751 | 100000 | 0 | 79242.6655 | 79242.6655 | 80339.6213 | 80339.6213 | 80272.2263 | 80272.2263 | 80276.3309 | 80276.3309 | 80276.0808 | 80276.0808 | 80276.096 | 80276.096 | 80276.0951 | 80276.0951 | 80276.0952 | 80276.0952 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN16 DN50 | 36.2 | 1.0089 | 0.03524 | 0.11982 |  | 10 | 0.03524 | 0.11982 | 3513.3979 | 7.466e-05 | 0.010657 | 100000 | 0 | 223.4669 | 223.4669 | 364.724 | 364.724 | 343.3607 | 343.3607 | 345.8604 | 345.8604 | 345.5581 | 345.5581 | 345.5945 | 345.5945 | 345.5901 | 345.5901 | 345.5907 | 345.5907 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 10.5791 | 10.7421 | 36.5232 |  | 10 | 10.7421 | 36.5232 | 1205649.6898 | 0.00023299 | 0.058751 | 100000 | 0 | 105656.8874 | 105656.8874 | 105328.5819 | 105328.5819 | 105346.9743 | 105346.9743 | 105345.9418 | 105345.9418 | 105345.9998 | 105345.9998 | 105345.9965 | 105345.9965 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN16 DN63 | 45.8 | 0.71579 | 0.014276 | 0.057103 |  | 10 | 0.014276 | 0.057103 | 1397.9245 | 5.9011e-05 | 0.0074887 | 100000 | 0 | 83.8733 | 83.8733 | 149.5724 | 149.5724 | 138.8437 | 138.8437 | 140.145 | 140.145 | 139.9806 | 139.9806 | 140.0013 | 140.0013 | 139.9987 | 139.9987 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN16 DN110 | 79.8 | 0.24488 | 0.0010751 | 0.0017202 |  | 10 | 0.0010751 | 0.0017202 | 93.9027 | 3.3868e-05 | 0.0032561 | 100000 | 0 | 4.9513 | 4.9513 | 11.7686 | 11.7686 | 10.3821 | 10.3821 | 10.5661 | 10.5661 | 10.54 | 10.54 | 10.5437 | 10.5437 | 10.5432 | 10.5432 | 10.5433 | 10.5433 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 7.4806 | 5.5927 | 19.0152 |  | 10 | 5.5927 | 19.0152 | 602824.8449 | 0.00023299 | 0.058751 | 100000 | 0 | 52828.4437 | 52828.4437 | 54987.1716 | 54987.1716 | 54837.0855 | 54837.0855 | 54847.2628 | 54847.2628 | 54846.5715 | 54846.5715 | 54846.6185 | 54846.6185 | 54846.6153 | 54846.6153 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155 | 54846.6155
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN16 DN40 | 29 | 1.3247 | 0.075566 | 0.25692 |  | 10 | 0.075566 | 0.25692 | 7561.8349 | 9.3197e-05 | 0.014863 | 100000 | 0 | 509.2963 | 509.2963 | 774.8766 | 774.8766 | 737.243 | 737.243 | 741.5068 | 741.5068 | 741.0102 | 741.0102 | 741.0679 | 741.0679 | 741.0612 | 741.0612 | 741.062 | 741.062 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619 | 741.0619
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 9.1618 | 8.1858 | 27.8316 |  | 10 | 8.1858 | 27.8316 | 904237.2674 | 0.00023299 | 0.058751 | 100000 | 0 | 79242.6655 | 79242.6655 | 80339.6213 | 80339.6213 | 80272.2263 | 80272.2263 | 80276.3309 | 80276.3309 | 80276.0808 | 80276.0808 | 80276.096 | 80276.096 | 80276.0951 | 80276.0951 | 80276.0952 | 80276.0952 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951 | 80276.0951
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN16 DN50 | 36.2 | 1.0089 | 0.03524 | 0.11982 |  | 10 | 0.03524 | 0.11982 | 3513.3979 | 7.466e-05 | 0.010657 | 100000 | 0 | 223.4669 | 223.4669 | 364.724 | 364.724 | 343.3607 | 343.3607 | 345.8604 | 345.8604 | 345.5581 | 345.5581 | 345.5945 | 345.5945 | 345.5901 | 345.5901 | 345.5907 | 345.5907 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906 | 345.5906
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN16 DN16 | 11.6 | 10.5791 | 10.7421 | 36.5232 |  | 10 | 10.7421 | 36.5232 | 1205649.6898 | 0.00023299 | 0.058751 | 100000 | 0 | 105656.8874 | 105656.8874 | 105328.5819 | 105328.5819 | 105346.9743 | 105346.9743 | 105345.9418 | 105345.9418 | 105345.9998 | 105345.9998 | 105345.9965 | 105345.9965 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967 | 105345.9967
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN16 DN63 | 45.8 | 0.71579 | 0.014276 | 0.057103 |  | 10 | 0.014276 | 0.057103 | 1397.9245 | 5.9011e-05 | 0.0074887 | 100000 | 0 | 83.8733 | 83.8733 | 149.5724 | 149.5724 | 138.8437 | 138.8437 | 140.145 | 140.145 | 139.9806 | 139.9806 | 140.0013 | 140.0013 | 139.9987 | 139.9987 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999 | 139.999
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN16 DN110 | 79.8 | 0.24488 | 0.0010751 | 0.0017202 |  | 10 | 0.0010751 | 0.0017202 | 93.9027 | 3.3868e-05 | 0.0032561 | 100000 | 0 | 4.9513 | 4.9513 | 11.7686 | 11.7686 | 10.3821 | 10.3821 | 10.5661 | 10.5661 | 10.54 | 10.54 | 10.5437 | 10.5437 | 10.5432 | 10.5432 | 10.5433 | 10.5433 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN16 DN110 | 79.8 | 0.24488 | 0.0010751 | 0.0017202 |  | 10 | 0.0010751 | 0.0017202 | 93.9027 | 3.3868e-05 | 0.0032561 | 100000 | 0 | 4.9513 | 4.9513 | 11.7686 | 11.7686 | 10.3821 | 10.3821 | 10.5661 | 10.5661 | 10.54 | 10.54 | 10.5437 | 10.5437 | 10.5432 | 10.5432 | 10.5433 | 10.5433 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432 | 10.5432
[7 empty] | SH = | 98.0301 | m

## PPR RC
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
| DIMENZIONISANJE VODOVODNE MREŽE | [8 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.0115 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Greenlife PP-RC PN20 DN20 | 13.2 | 1.2918 | 0.19524 | 0.25381 |  | 10 | 0.19524 | 0.25381 | 15797.2481 | 0.00023546 | 0.0484 | 100000 | 0 | 1358.0694 | 1358.0694 | 2000.6372 | 2000.6372 | 1904.254 | 1904.254 | 1915.9769 | 1915.9769 | 1914.5111 | 1914.5111 | 1914.6938 | 1914.6938 | 1914.671 | 1914.671 | 1914.6738 | 1914.6738 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735 | 1914.6735
2-3 | 4.8 | 1 | 0.25 | Pipelife Greenlife PP-RC PN20 DN40 | 26.6 | 0.44987 | 0.012509 | 0.060042 |  | 10 | 0.012509 | 0.060042 | 950.7644 | 0.00011685 | 0.016919 | 100000 | 0 | 66.9421 | 66.9421 | 134.3118 | 134.3118 | 121.0773 | 121.0773 | 122.9034 | 122.9034 | 122.6369 | 122.6369 | 122.6755 | 122.6755 | 122.6699 | 122.6699 | 122.6707 | 122.6707 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706 | 122.6706
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Greenlife PP-RC PN20 DN25 | 16.6 | 1.2915 | 0.14604 | 0.24826 |  | 10 | 0.14604 | 0.24826 | 12555.9814 | 0.00018724 | 0.034319 | 100000 | 0 | 1008.1694 | 1008.1694 | 1496.2361 | 1496.2361 | 1424.5818 | 1424.5818 | 1433.0825 | 1433.0825 | 1432.0459 | 1432.0459 | 1432.1719 | 1432.1719 | 1432.1566 | 1432.1566 | 1432.1585 | 1432.1585 | 1432.1582 | 1432.1582 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583 | 1432.1583
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Greenlife PP-RC PN20 DN32 | 21.2 | 0.86741 | 0.052888 | 0.063466 |  | 10 | 0.052888 | 0.063466 | 4434.9941 | 0.00014661 | 0.023779 | 100000 | 0 | 332.1615 | 332.1615 | 550.5519 | 550.5519 | 514.662 | 514.662 | 519.1851 | 519.1851 | 518.5936 | 518.5936 | 518.6706 | 518.6706 | 518.6605 | 518.6605 | 518.6619 | 518.6619 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617 | 518.6617
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Greenlife PP-RC PN20 DN75 | 50 | 0.19099 | 0.0012614 | 0.0042886 |  | 10 | 0.0012614 | 0.0042886 | 91.1619 | 6.2162e-05 | 0.0065652 | 100000 | 0 | 5.4728 | 5.4728 | 14.1041 | 14.1041 | 12.1227 | 12.1227 | 12.4087 | 12.4087 | 12.3639 | 12.3639 | 12.3708 | 12.3708 | 12.3698 | 12.3698 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699 | 12.3699
6-7 | 3.4 | 5 | 0.55902 | Pipelife Greenlife PP-RC PN20 DN63 | 42 | 0.40349 | 0.005797 | 0.01971 |  | 10 | 0.005797 | 0.01971 | 484.4006 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 30.3386 | 30.3386 | 62.2343 | 62.2343 | 56.1397 | 56.1397 | 56.9503 | 56.9503 | 56.8363 | 56.8363 | 56.8522 | 56.8522 | 56.85 | 56.85 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503 | 56.8503
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Greenlife PP-RC PN20 DN20 | 13.2 | 4.9189 | 2.2131 | 7.5245 |  | 10 | 2.2131 | 7.5245 | 229060.0967 | 0.00023546 | 0.0484 | 100000 | 0 | 19692.0065 | 19692.0065 | 21870.1726 | 21870.1726 | 21690.2636 | 21690.2636 | 21704.2078 | 21704.2078 | 21703.1215 | 21703.1215 | 21703.2061 | 21703.2061 | 21703.1995 | 21703.1995 | 21703.2001 | 21703.2001 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2 | 21703.2
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PP-RC PN20 DN25 | 16.6 | 3.6529 | 0.95976 | 3.2632 |  | 10 | 0.95976 | 3.2632 | 100447.8508 | 0.00018724 | 0.034319 | 100000 | 0 | 8065.3549 | 8065.3549 | 9541.5508 | 9541.5508 | 9401.059 | 9401.059 | 9413.173 | 9413.173 | 9412.1192 | 9412.1192 | 9412.2108 | 9412.2108 | 9412.2029 | 9412.2029 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PP-RC PN20 DN32 | 21.2 | 2.4788 | 0.34819 | 1.1838 |  | 10 | 0.34819 | 1.1838 | 36219.1183 | 0.00014661 | 0.023779 | 100000 | 0 | 2712.6526 | 2712.6526 | 3494.1792 | 3494.1792 | 3406.942 | 3406.942 | 3415.3808 | 3415.3808 | 3414.5524 | 3414.5524 | 3414.6336 | 3414.6336 | 3414.6257 | 3414.6257 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PP-RC PN20 DN40 | 26.6 | 1.7423 | 0.13856 | 0.47109 |  | 10 | 0.13856 | 0.47109 | 14261.4658 | 0.00011685 | 0.016919 | 100000 | 0 | 1004.1309 | 1004.1309 | 1404.4868 | 1404.4868 | 1354.0143 | 1354.0143 | 1359.3075 | 1359.3075 | 1358.7408 | 1358.7408 | 1358.8014 | 1358.8014 | 1358.7949 | 1358.7949 | 1358.7956 | 1358.7956 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PP-RC PN20 DN50 | 33.2 | 1.1994 | 0.053718 | 0.18264 |  | 10 | 0.053718 | 0.18264 | 5414.767 | 9.3618e-05 | 0.012134 | 100000 | 0 | 359.7791 | 359.7791 | 551.0433 | 551.0433 | 524.0895 | 524.0895 | 527.1149 | 527.1149 | 526.7658 | 526.7658 | 526.8059 | 526.8059 | 526.8013 | 526.8013 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PP-RC PN20 DN63 | 42 | 0.80699 | 0.019747 | 0.067138 |  | 10 | 0.019747 | 0.067138 | 1937.6023 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 121.3542 | 121.3542 | 205.3761 | 205.3761 | 192.2662 | 192.2662 | 193.8215 | 193.8215 | 193.6302 | 193.6302 | 193.6536 | 193.6536 | 193.6508 | 193.6508 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PP-RC PN20 DN75 | 50 | 0.60059 | 0.0093994 | 0.037598 |  | 10 | 0.0093994 | 0.037598 | 901.4904 | 6.2162e-05 | 0.0065652 | 100000 | 0 | 54.1201 | 54.1201 | 98.831 | 98.831 | 91.3669 | 91.3669 | 92.2819 | 92.2819 | 92.1649 | 92.1649 | 92.1798 | 92.1798 | 92.1779 | 92.1779 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PP-RC PN20 DN90 | 60 | 0.43316 | 0.0041983 | 0.0067172 |  | 10 | 0.0041983 | 0.0067172 | 390.7834 | 5.1802e-05 | 0.0049943 | 100000 | 0 | 22.4722 | 22.4722 | 44.7074 | 44.7074 | 40.7274 | 40.7274 | 41.2307 | 41.2307 | 41.1638 | 41.1638 | 41.1726 | 41.1726 | 41.1714 | 41.1714 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PP-RC PN20 DN25 | 16.6 | 3.6529 | 0.95976 | 3.2632 |  | 10 | 0.95976 | 3.2632 | 100447.8508 | 0.00018724 | 0.034319 | 100000 | 0 | 8065.3549 | 8065.3549 | 9541.5508 | 9541.5508 | 9401.059 | 9401.059 | 9413.173 | 9413.173 | 9412.1192 | 9412.1192 | 9412.2108 | 9412.2108 | 9412.2029 | 9412.2029 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035 | 9412.2035
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PP-RC PN20 DN32 | 21.2 | 2.4788 | 0.34819 | 1.1838 |  | 10 | 0.34819 | 1.1838 | 36219.1183 | 0.00014661 | 0.023779 | 100000 | 0 | 2712.6526 | 2712.6526 | 3494.1792 | 3494.1792 | 3406.942 | 3406.942 | 3415.3808 | 3415.3808 | 3414.5524 | 3414.5524 | 3414.6336 | 3414.6336 | 3414.6257 | 3414.6257 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264 | 3414.6264
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PP-RC PN20 DN40 | 26.6 | 1.7423 | 0.13856 | 0.47109 |  | 10 | 0.13856 | 0.47109 | 14261.4658 | 0.00011685 | 0.016919 | 100000 | 0 | 1004.1309 | 1004.1309 | 1404.4868 | 1404.4868 | 1354.0143 | 1354.0143 | 1359.3075 | 1359.3075 | 1358.7408 | 1358.7408 | 1358.8014 | 1358.8014 | 1358.7949 | 1358.7949 | 1358.7956 | 1358.7956 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955 | 1358.7955
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PP-RC PN20 DN50 | 33.2 | 1.1994 | 0.053718 | 0.18264 |  | 10 | 0.053718 | 0.18264 | 5414.767 | 9.3618e-05 | 0.012134 | 100000 | 0 | 359.7791 | 359.7791 | 551.0433 | 551.0433 | 524.0895 | 524.0895 | 527.1149 | 527.1149 | 526.7658 | 526.7658 | 526.8059 | 526.8059 | 526.8013 | 526.8013 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018 | 526.8018
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PP-RC PN20 DN63 | 42 | 0.80699 | 0.019747 | 0.067138 |  | 10 | 0.019747 | 0.067138 | 1937.6023 | 7.4003e-05 | 0.0085276 | 100000 | 0 | 121.3542 | 121.3542 | 205.3761 | 205.3761 | 192.2662 | 192.2662 | 193.8215 | 193.8215 | 193.6302 | 193.6302 | 193.6536 | 193.6536 | 193.6508 | 193.6508 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511 | 193.6511
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PP-RC PN20 DN75 | 50 | 0.60059 | 0.0093994 | 0.037598 |  | 10 | 0.0093994 | 0.037598 | 901.4904 | 6.2162e-05 | 0.0065652 | 100000 | 0 | 54.1201 | 54.1201 | 98.831 | 98.831 | 91.3669 | 91.3669 | 92.2819 | 92.2819 | 92.1649 | 92.1649 | 92.1798 | 92.1798 | 92.1779 | 92.1779 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781 | 92.1781
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PP-RC PN20 DN90 | 60 | 0.43316 | 0.0041983 | 0.0067172 |  | 10 | 0.0041983 | 0.0067172 | 390.7834 | 5.1802e-05 | 0.0049943 | 100000 | 0 | 22.4722 | 22.4722 | 44.7074 | 44.7074 | 40.7274 | 40.7274 | 41.2307 | 41.2307 | 41.1638 | 41.1638 | 41.1726 | 41.1726 | 41.1714 | 41.1714 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PP-RC PN20 DN90 | 60 | 0.43316 | 0.0041983 | 0.0067172 |  | 10 | 0.0041983 | 0.0067172 | 390.7834 | 5.1802e-05 | 0.0049943 | 100000 | 0 | 22.4722 | 22.4722 | 44.7074 | 44.7074 | 40.7274 | 40.7274 | 41.2307 | 41.2307 | 41.1638 | 41.1638 | 41.1726 | 41.1726 | 41.1714 | 41.1714 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716 | 41.1716
[7 empty] | SH = | 13.3863 | m

## PPR CARBO
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
| DIMENZIONISANJE VODOVODNE MREŽE | [8 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.0115 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 1.0855 | 0.12837 | 0.16688 |  | 10 | 0.12837 | 0.16688 | 10224.4189 | 0.00021584 | 0.042477 | 100000 | 0 | 856.1702 | 856.1702 | 1324.9467 | 1324.9467 | 1250.6566 | 1250.6566 | 1259.9797 | 1259.9797 | 1258.7715 | 1258.7715 | 1258.9275 | 1258.9275 | 1258.9073 | 1258.9073 | 1258.9099 | 1258.9099 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096 | 1258.9096
2-3 | 4.8 | 1 | 0.25 | Pipelife Carbo PP-RCT PN10 DN25 PN10 | 18 | 0.98244 | 0.081082 | 0.3892 |  | 10 | 0.081082 | 0.3892 | 6700.6751 | 0.00017267 | 0.030394 | 100000 | 0 | 525.5797 | 525.5797 | 840.0014 | 840.0014 | 789.5739 | 789.5739 | 795.8823 | 795.8823 | 795.0657 | 795.0657 | 795.1709 | 795.1709 | 795.1573 | 795.1573 | 795.1591 | 795.1591 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589 | 795.1589
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 1.7162 | 0.29057 | 0.49398 |  | 10 | 0.29057 | 0.49398 | 25561.0472 | 0.00021584 | 0.042477 | 100000 | 0 | 2140.4255 | 2140.4255 | 2946.3991 | 2946.3991 | 2838.7929 | 2838.7929 | 2850.8365 | 2850.8365 | 2849.4598 | 2849.4598 | 2849.6168 | 2849.6168 | 2849.5989 | 2849.5989 | 2849.6009 | 2849.6009 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007 | 2849.6007
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Carbo PP-RCT PN10 DN50 PN10 | 36.2 | 0.29749 | 0.0041094 | 0.0049313 |  | 10 | 0.0041094 | 0.0049313 | 305.5129 | 8.5859e-05 | 0.010657 | 100000 | 0 | 19.8574 | 19.8574 | 44.9862 | 44.9862 | 39.6439 | 39.6439 | 40.3996 | 40.3996 | 40.2852 | 40.2852 | 40.3023 | 40.3023 | 40.2998 | 40.2998 | 40.3002 | 40.3002 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001 | 40.3001
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Carbo PP-RCT PN10 DN40 PN10 | 29 | 0.56773 | 0.016857 | 0.057315 |  | 10 | 0.016857 | 0.057315 | 1388.9084 | 0.00010718 | 0.014863 | 100000 | 0 | 95.5811 | 95.5811 | 178.6215 | 178.6215 | 163.5774 | 163.5774 | 165.5554 | 165.5554 | 165.2826 | 165.2826 | 165.32 | 165.32 | 165.3149 | 165.3149 | 165.3156 | 165.3156 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155 | 165.3155
6-7 | 3.4 | 5 | 0.55902 | Pipelife Carbo PP-RCT PN10 DN90 PN10 | 69.8 | 0.14609 | 0.00051812 | 0.0017616 |  | 10 | 0.00051812 | 0.0017616 | 38.2097 | 4.4529e-05 | 0.0039803 | 100000 | 0 | 2.1222 | 2.1222 | 5.8465 | 5.8465 | 4.9729 | 4.9729 | 5.0981 | 5.0981 | 5.0785 | 5.0785 | 5.0815 | 5.0815 | 5.0811 | 5.0811 | 5.0812 | 5.0812 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811 | 5.0811
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Carbo PP-RCT PN10 DN75 PN10 | 56.2 | 0.27136 | 0.0020036 | 0.0068123 |  | 10 | 0.0020036 | 0.0068123 | 163.7335 | 5.5304e-05 | 0.0055093 | 100000 | 0 | 9.5607 | 9.5607 | 21.8749 | 21.8749 | 19.3493 | 19.3493 | 19.6928 | 19.6928 | 19.6429 | 19.6429 | 19.6501 | 19.6501 | 19.649 | 19.649 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492 | 19.6492
8-9 | 3.4 | 10 | 0.79057 | Pipelife Carbo PP-RCT PN10 DN63 PN10 | 45.8 | 0.47987 | 0.0057564 | 0.019572 |  | 50 | 0.0057564 | 0.019572 | 620.9888 | 6.7863e-05 | 0.0031141 | 100000 | 0 | 36.7706 | 36.7706 | 59.3192 | 59.3192 | 56.1396 | 56.1396 | 56.4877 | 56.4877 | 56.4484 | 56.4484 | 56.4528 | 56.4528 | 56.4523 | 56.4523 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524 | 56.4524
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Carbo PP-RCT PN10 DN40 PN10 | 29 | 1.3247 | 0.075967 | 0.25829 |  | 10 | 0.075967 | 0.25829 | 7561.8349 | 0.00010718 | 0.014863 | 100000 | 0 | 520.3862 | 520.3862 | 776.8556 | 776.8556 | 741.4567 | 741.4567 | 745.3956 | 745.3956 | 744.9457 | 744.9457 | 744.997 | 744.997 | 744.9911 | 744.9911 | 744.9918 | 744.9918 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917
10-11 | 3.4 | 15 | 0.96825 | Pipelife Carbo PP-RCT PN10 DN25 PN10 | 18 | 3.805 | 0.93557 | 3.1809 |  | 10 | 0.93557 | 3.1809 | 100510.1272 | 0.00017267 | 0.030394 | 100000 | 0 | 7883.6959 | 7883.6959 | 9295.9319 | 9295.9319 | 9164.7325 | 9164.7325 | 9175.7941 | 9175.7941 | 9174.8536 | 9174.8536 | 9174.9335 | 9174.9335 | 9174.9267 | 9174.9267 | 9174.9273 | 9174.9273 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272 | 9174.9272
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Carbo PP-RCT PN10 DN110 PN10 | 85.4 | 0.18127 | 0.00058389 | 0.0019852 |  | 10 | 0.00058389 | 0.0019852 | 48.0818 | 3.6395e-05 | 0.0029411 | 100000 | 0 | 2.5526 | 2.5526 | 6.4681 | 6.4681 | 5.626 | 5.626 | 5.7409 | 5.7409 | 5.724 | 5.724 | 5.7264 | 5.7264 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261
12-13 | 3.4 | 20 | 1.118 | Pipelife Carbo PP-RCT PN10 DN125 PN10 | 97 | 0.15129 | 0.0003627 | 0.0012332 |  | 10 | 0.0003627 | 0.0012332 | 29.4885 | 3.2042e-05 | 0.0024297 | 100000 | 0 | 1.5225 | 1.5225 | 4.0489 | 4.0489 | 3.4901 | 3.4901 | 3.5668 | 3.5668 | 3.5554 | 3.5554 | 3.5571 | 3.5571 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569
13-14 | 4 | 22.25 | 1.1792 | Pipelife Carbo PP-RCT PN10 DN75 PN10 | 56.2 | 0.47538 | 0.0053696 | 0.021478 |  | 10 | 0.0053696 | 0.021478 | 502.4924 | 5.5304e-05 | 0.0055093 | 100000 | 0 | 29.3416 | 29.3416 | 56.9796 | 56.9796 | 52.1189 | 52.1189 | 52.7293 | 52.7293 | 52.6489 | 52.6489 | 52.6594 | 52.6594 | 52.658 | 52.658 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582
14-15 | 1.6 | 24 | 1.2247 | Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 7.5202 | 4.3904 | 7.0246 |  | 10 | 4.3904 | 7.0246 | 490772.1057 | 0.00021584 | 0.042477 | 100000 | 0 | 41096.1689 | 41096.1689 | 43182.1185 | 43182.1185 | 43047.6132 | 43047.6132 | 43056.0197 | 43056.0197 | 43055.4932 | 43055.4932 | 43055.5262 | 43055.5262 | 43055.5241 | 43055.5241 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242
8-9 | 3.4 | 10 | 0.79057 | Pipelife Carbo PP-RCT PN10 DN63 PN10 | 45.8 | 0.47987 | 0.0070525 | 0.023979 |  | 10 | 0.0070525 | 0.023979 | 628.2807 | 6.7863e-05 | 0.0074887 | 100000 | 0 | 38.5249 | 38.5249 | 74.9801 | 74.9801 | 68.4216 | 68.4216 | 69.263 | 69.263 | 69.1496 | 69.1496 | 69.1648 | 69.1648 | 69.1627 | 69.1627 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163 | 69.163
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Carbo PP-RCT PN10 DN40 PN10 | 29 | 1.3247 | 0.075967 | 0.25829 |  | 10 | 0.075967 | 0.25829 | 7561.8349 | 0.00010718 | 0.014863 | 100000 | 0 | 520.3862 | 520.3862 | 776.8556 | 776.8556 | 741.4567 | 741.4567 | 745.3956 | 745.3956 | 744.9457 | 744.9457 | 744.997 | 744.997 | 744.9911 | 744.9911 | 744.9918 | 744.9918 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917 | 744.9917
10-11 | 3.4 | 15 | 0.96825 | Pipelife Carbo PP-RCT PN10 DN50 PN10 | 36.2 | 0.94076 | 0.031235 | 0.1062 |  | 10 | 0.031235 | 0.1062 | 3055.1286 | 8.5859e-05 | 0.010657 | 100000 | 0 | 198.5741 | 198.5741 | 323.1815 | 323.1815 | 304.3445 | 304.3445 | 306.5489 | 306.5489 | 306.2823 | 306.2823 | 306.3144 | 306.3144 | 306.3105 | 306.3105 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311 | 306.311
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Carbo PP-RCT PN10 DN110 PN10 | 85.4 | 0.18127 | 0.00058389 | 0.0019852 |  | 10 | 0.00058389 | 0.0019852 | 48.0818 | 3.6395e-05 | 0.0029411 | 100000 | 0 | 2.5526 | 2.5526 | 6.4681 | 6.4681 | 5.626 | 5.626 | 5.7409 | 5.7409 | 5.724 | 5.724 | 5.7264 | 5.7264 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261 | 5.7261
12-13 | 3.4 | 20 | 1.118 | Pipelife Carbo PP-RCT PN10 DN125 PN10 | 97 | 0.15129 | 0.0003627 | 0.0012332 |  | 10 | 0.0003627 | 0.0012332 | 29.4885 | 3.2042e-05 | 0.0024297 | 100000 | 0 | 1.5225 | 1.5225 | 4.0489 | 4.0489 | 3.4901 | 3.4901 | 3.5668 | 3.5668 | 3.5554 | 3.5554 | 3.5571 | 3.5571 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569 | 3.5569
13-14 | 4 | 22.25 | 1.1792 | Pipelife Carbo PP-RCT PN10 DN75 PN10 | 56.2 | 0.47538 | 0.0053696 | 0.021478 |  | 10 | 0.0053696 | 0.021478 | 502.4924 | 5.5304e-05 | 0.0055093 | 100000 | 0 | 29.3416 | 29.3416 | 56.9796 | 56.9796 | 52.1189 | 52.1189 | 52.7293 | 52.7293 | 52.6489 | 52.6489 | 52.6594 | 52.6594 | 52.658 | 52.658 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582 | 52.6582
14-15 | 1.6 | 24 | 1.2247 | Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 7.5202 | 4.3904 | 7.0246 |  | 10 | 4.3904 | 7.0246 | 490772.1057 | 0.00021584 | 0.042477 | 100000 | 0 | 41096.1689 | 41096.1689 | 43182.1185 | 43182.1185 | 43047.6132 | 43047.6132 | 43056.0197 | 43056.0197 | 43055.4932 | 43055.4932 | 43055.5262 | 43055.5262 | 43055.5241 | 43055.5241 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242
14-15 | 1.6 | 24 | 1.2247 | Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 7.5202 | 4.3904 | 7.0246 |  | 10 | 4.3904 | 7.0246 | 490772.1057 | 0.00021584 | 0.042477 | 100000 | 0 | 41096.1689 | 41096.1689 | 43182.1185 | 43182.1185 | 43047.6132 | 43047.6132 | 43056.0197 | 43056.0197 | 43055.4932 | 43055.4932 | 43055.5262 | 43055.5262 | 43055.5241 | 43055.5241 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242 | 43055.5242
[7 empty] | SH = | 11.629 | m

## UNIBETA
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
| DIMENZIONISANJE VODOVODNE MREŽE | [8 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.0115 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Unibeta PP-RCT PN10 DN16 PN10 | 11.6 | 1.6727 | 0.36471 | 0.47412 |  | 10 | 0.36471 | 0.47412 | 30141.2422 | 0.00026794 | 0.058751 | 100000 | 0 | 2696.7152 | 2696.7152 | 3700.2005 | 3700.2005 | 3562.4112 | 3562.4112 | 3578.2978 | 3578.2978 | 3576.4262 | 3576.4262 | 3576.6461 | 3576.6461 | 3576.6203 | 3576.6203 | 3576.6233 | 3576.6233 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623 | 3576.623
2-3 | 4.8 | 1 | 0.25 | Pipelife Unibeta PP-RCT PN10 DN63 PN10 | 48.8 | 0.13366 | 0.00070318 | 0.0033753 |  | 10 | 0.00070318 | 0.0033753 | 45.749 | 6.3691e-05 | 0.0068088 | 100000 | 0 | 2.7626 | 2.7626 | 8.0706 | 8.0706 | 6.721 | 6.721 | 6.9252 | 6.9252 | 6.8912 | 6.8912 | 6.8968 | 6.8968 | 6.8958 | 6.8958 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896 | 6.896
3-4 | 1.7 | 1.25 | 0.27951 | Pipelife Unibeta PP-RCT PN10 DN25 PN10 | 19.4 | 0.94559 | 0.068927 | 0.11718 |  | 10 | 0.068927 | 0.11718 | 5759.4691 | 0.00016021 | 0.027164 | 100000 | 0 | 442.2227 | 442.2227 | 715.0625 | 715.0625 | 671.0798 | 671.0798 | 676.5802 | 676.5802 | 675.8678 | 675.8678 | 675.9596 | 675.9596 | 675.9478 | 675.9478 | 675.9493 | 675.9493 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491 | 675.9491
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Unibeta PP-RCT PN10 DN32 PN10 | 24.8 | 0.63386 | 0.024939 | 0.029927 |  | 10 | 0.024939 | 0.029927 | 2024.4821 | 0.00012533 | 0.018794 | 100000 | 0 | 145.2468 | 145.2468 | 263.1909 | 263.1909 | 242.1406 | 242.1406 | 244.9053 | 244.9053 | 244.5253 | 244.5253 | 244.5772 | 244.5772 | 244.5702 | 244.5702 | 244.5711 | 244.5711 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571 | 244.571
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 0.49684 | 0.012257 | 0.041675 |  | 10 | 0.012257 | 0.041675 | 995.0734 | 0.00010026 | 0.013448 | 100000 | 0 | 67.2966 | 67.2966 | 130.6703 | 130.6703 | 118.8188 | 118.8188 | 120.3995 | 120.3995 | 120.1776 | 120.1776 | 120.2085 | 120.2085 | 120.2042 | 120.2042 | 120.2048 | 120.2048 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047 | 120.2047
6-7 | 3.4 | 5 | 0.55902 | Pipelife Unibeta PP-RCT PN10 DN63 PN10 | 48.8 | 0.29888 | 0.0028355 | 0.0096408 |  | 10 | 0.0028355 | 0.0096408 | 228.7452 | 6.3691e-05 | 0.0068088 | 100000 | 0 | 13.8128 | 13.8128 | 30.8676 | 30.8676 | 27.3939 | 27.3939 | 27.8679 | 27.8679 | 27.7989 | 27.7989 | 27.8089 | 27.8089 | 27.8074 | 27.8074 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076 | 27.8076
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Unibeta PP-RCT PN10 DN200 PN10 | 163.6 | 0.032022 | 1.2767e-05 | 4.3408e-05 |  | 10 | 1.2767e-05 | 4.3408e-05 | 0.78325 | 1.8998e-05 | 0.0011092 | 100000 | 0 | 0.03626 | 0.03626 | 0.15704 | 0.15704 | 0.12045 | 0.12045 | 0.12605 | 0.12605 | 0.12506 | 0.12506 | 0.12523 | 0.12523 | 0.1252 | 0.1252 | 0.12521 | 0.12521 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252 | 0.1252
8-9 | 3.4 | 10 | 0.79057 | Pipelife Unibeta PP-RCT PN10 DN160 PN10 | 130.8 | 0.058835 | 4.8297e-05 | 0.00016421 |  | 10 | 4.8297e-05 | 0.00016421 | 3.3071 | 2.3762e-05 | 0.0015516 | 100000 | 0 | 0.16026 | 0.16026 | 0.56987 | 0.56987 | 0.45972 | 0.45972 | 0.47595 | 0.47595 | 0.47327 | 0.47327 | 0.4737 | 0.4737 | 0.47363 | 0.47363 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.1593 | 0.055042 | 0.18714 |  | 10 | 0.055042 | 0.18714 | 5417.6221 | 0.00010026 | 0.013448 | 100000 | 0 | 366.3923 | 366.3923 | 565.433 | 565.433 | 536.8708 | 536.8708 | 540.1234 | 540.1234 | 539.7423 | 539.7423 | 539.7868 | 539.7868 | 539.7816 | 539.7816 | 539.7822 | 539.7822 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821
10-11 | 3.4 | 15 | 0.96825 | Pipelife Unibeta PP-RCT PN10 DN110 PN10 | 85.4 | 0.16904 | 0.00051687 | 0.0017574 |  | 10 | 0.00051687 | 0.0017574 | 41.8103 | 3.6395e-05 | 0.0029411 | 100000 | 0 | 2.2196 | 2.2196 | 5.7494 | 5.7494 | 4.9763 | 4.9763 | 5.0827 | 5.0827 | 5.0669 | 5.0669 | 5.0692 | 5.0692 | 5.0688 | 5.0688 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Unibeta PP-RCT PN10 DN75 PN10 | 58.2 | 0.3903 | 0.0036289 | 0.012338 |  | 10 | 0.0036289 | 0.012338 | 327.081 | 5.3404e-05 | 0.0052278 | 100000 | 0 | 18.9431 | 18.9431 | 38.8513 | 38.8513 | 35.1703 | 35.1703 | 35.6444 | 35.6444 | 35.58 | 35.58 | 35.5887 | 35.5887 | 35.5875 | 35.5875 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877
12-13 | 3.4 | 20 | 1.118 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.4813 | 0.085487 | 0.29065 |  | 10 | 0.085487 | 0.29065 | 8845.0973 | 0.00010026 | 0.013448 | 100000 | 0 | 598.1916 | 598.1916 | 870.8313 | 870.8313 | 834.8635 | 834.8635 | 838.7355 | 838.7355 | 838.3087 | 838.3087 | 838.3556 | 838.3556 | 838.3504 | 838.3504 | 838.351 | 838.351 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509
13-14 | 4 | 22.25 | 1.1792 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.5624 | 0.094111 | 0.37644 |  | 10 | 0.094111 | 0.37644 | 9840.1708 | 0.00010026 | 0.013448 | 100000 | 0 | 665.4881 | 665.4881 | 957.0534 | 957.0534 | 919.3101 | 919.3101 | 923.3205 | 923.3205 | 922.8846 | 922.8846 | 922.9319 | 922.9319 | 922.9268 | 922.9268 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273
14-15 | 1.6 | 24 | 1.2247 | Pipelife Unibeta PP-RCT PN10 DN32 PN10 | 24.8 | 2.5354 | 0.29867 | 0.47787 |  | 10 | 0.29867 | 0.47787 | 32391.7138 | 0.00012533 | 0.018794 | 100000 | 0 | 2323.9482 | 2323.9482 | 2996.1359 | 2996.1359 | 2922.6352 | 2922.6352 | 2929.5966 | 2929.5966 | 2928.9278 | 2928.9278 | 2928.9919 | 2928.9919 | 2928.9858 | 2928.9858 | 2928.9864 | 2928.9864 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863
8-9 | 3.4 | 10 | 0.79057 | Pipelife Unibeta PP-RCT PN10 DN160 PN10 | 130.8 | 0.058835 | 4.8297e-05 | 0.00016421 |  | 10 | 4.8297e-05 | 0.00016421 | 3.3071 | 2.3762e-05 | 0.0015516 | 100000 | 0 | 0.16026 | 0.16026 | 0.56987 | 0.56987 | 0.45972 | 0.45972 | 0.47595 | 0.47595 | 0.47327 | 0.47327 | 0.4737 | 0.4737 | 0.47363 | 0.47363 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364 | 0.47364
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.1593 | 0.055042 | 0.18714 |  | 10 | 0.055042 | 0.18714 | 5417.6221 | 0.00010026 | 0.013448 | 100000 | 0 | 366.3923 | 366.3923 | 565.433 | 565.433 | 536.8708 | 536.8708 | 540.1234 | 540.1234 | 539.7423 | 539.7423 | 539.7868 | 539.7868 | 539.7816 | 539.7816 | 539.7822 | 539.7822 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821 | 539.7821
10-11 | 3.4 | 15 | 0.96825 | Pipelife Unibeta PP-RCT PN10 DN110 PN10 | 85.4 | 0.16904 | 0.00051687 | 0.0017574 |  | 10 | 0.00051687 | 0.0017574 | 41.8103 | 3.6395e-05 | 0.0029411 | 100000 | 0 | 2.2196 | 2.2196 | 5.7494 | 5.7494 | 4.9763 | 4.9763 | 5.0827 | 5.0827 | 5.0669 | 5.0669 | 5.0692 | 5.0692 | 5.0688 | 5.0688 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689 | 5.0689
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Unibeta PP-RCT PN10 DN75 PN10 | 58.2 | 0.3903 | 0.0036289 | 0.012338 |  | 10 | 0.0036289 | 0.012338 | 327.081 | 5.3404e-05 | 0.0052278 | 100000 | 0 | 18.9431 | 18.9431 | 38.8513 | 38.8513 | 35.1703 | 35.1703 | 35.6444 | 35.6444 | 35.58 | 35.58 | 35.5887 | 35.5887 | 35.5875 | 35.5875 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877 | 35.5877
12-13 | 3.4 | 20 | 1.118 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.4813 | 0.085487 | 0.29065 |  | 10 | 0.085487 | 0.29065 | 8845.0973 | 0.00010026 | 0.013448 | 100000 | 0 | 598.1916 | 598.1916 | 870.8313 | 870.8313 | 834.8635 | 834.8635 | 838.7355 | 838.7355 | 838.3087 | 838.3087 | 838.3556 | 838.3556 | 838.3504 | 838.3504 | 838.351 | 838.351 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509 | 838.3509
13-14 | 4 | 22.25 | 1.1792 | Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 1.5624 | 0.094111 | 0.37644 |  | 10 | 0.094111 | 0.37644 | 9840.1708 | 0.00010026 | 0.013448 | 100000 | 0 | 665.4881 | 665.4881 | 957.0534 | 957.0534 | 919.3101 | 919.3101 | 923.3205 | 923.3205 | 922.8846 | 922.8846 | 922.9319 | 922.9319 | 922.9268 | 922.9268 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273 | 922.9273
14-15 | 1.6 | 24 | 1.2247 | Pipelife Unibeta PP-RCT PN10 DN32 PN10 | 24.8 | 2.5354 | 0.29867 | 0.47787 |  | 10 | 0.29867 | 0.47787 | 32391.7138 | 0.00012533 | 0.018794 | 100000 | 0 | 2323.9482 | 2323.9482 | 2996.1359 | 2996.1359 | 2922.6352 | 2922.6352 | 2929.5966 | 2929.5966 | 2928.9278 | 2928.9278 | 2928.9919 | 2928.9919 | 2928.9858 | 2928.9858 | 2928.9864 | 2928.9864 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863
14-15 | 1.6 | 24 | 1.2247 | Pipelife Unibeta PP-RCT PN10 DN32 PN10 | 24.8 | 2.5354 | 0.29867 | 0.47787 |  | 10 | 0.29867 | 0.47787 | 32391.7138 | 0.00012533 | 0.018794 | 100000 | 0 | 2323.9482 | 2323.9482 | 2996.1359 | 2996.1359 | 2922.6352 | 2922.6352 | 2929.5966 | 2929.5966 | 2928.9278 | 2928.9278 | 2928.9919 | 2928.9919 | 2928.9858 | 2928.9858 | 2928.9864 | 2928.9864 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863 | 2928.9863
[7 empty] | SH = | 2.0223 | m

## PPR PN10
[13 empty] | °C | rho | viscosity | k | Pi | bar_to_meter
DIMENZIONISANJE VODOVODNE MREŽE | [9 empty] | temperature |  |  | 10 | 999.7026 | 1.308e-06 | 0.01 | 3.1416 | 10.197
Hidraulički gubici pritiska za vertikale | [12 empty] | 50 | 988.1 | 5.471e-07 | 0.01 | 3.1416 | 10.197
[13 empty] | 80 | 971.8 | 3.55e-07 | 0.01 | 3.1416 | 10.197
Deonica | L | JO | q | DN | Dunutrašnji | v | h | H |  | Temperatura | h = i | H | a | b | c | oldP | newP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP | newP | oldP
| (m) |  | (l/s) | (mm) | (mm) | (m/s) | (m/m) | (m) |  | °C | m/m | m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1-2 | 1.3 | 0.5 | 0.17678 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 0.85764 | 0.07257 | 0.094341 |  | 10 | 0.07257 | 0.094341 | 5673.8261 | 0.00016683 | 0.035598 | 100000 | 0 | 449.2608 | 449.2608 | 759.2374 | 759.2374 | 705.4388 | 705.4388 | 712.538 | 712.538 | 711.5628 | 711.5628 | 711.696 | 711.696 | 711.6778 | 711.6778 | 711.6803 | 711.6803 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68 | 711.68
2-3 | 4.8 | 1 | 0.25 | Pipelife Greenlife PPR PN10 DN25 | 20.4 | 0.76487 | 0.044288 | 0.21258 |  | 10 | 0.044288 | 0.21258 | 3583.6885 | 0.00013249 | 0.025192 | 100000 | 0 | 265.5848 | 265.5848 | 465.3318 | 465.3318 | 430.2799 | 430.2799 | 434.8797 | 434.8797 | 434.2498 | 434.2498 | 434.3356 | 434.3356 | 434.3239 | 434.3239 | 434.3255 | 434.3255 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253 | 434.3253
3-4 | 1.7 | 2 | 0.35355 | Pipelife Greenlife PPR PN10 DN32 | 26.2 | 0.65579 | 0.02462 | 0.041854 |  | 10 | 0.02462 | 0.041854 | 2051.184 | 0.00010316 | 0.017308 | 100000 | 0 | 141.9258 | 141.9258 | 260.1438 | 260.1438 | 239.0116 | 239.0116 | 241.7792 | 241.7792 | 241.3997 | 241.3997 | 241.4514 | 241.4514 | 241.4444 | 241.4444 | 241.4453 | 241.4453 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452 | 241.4452
4-5 | 1.2 | 1.5 | 0.30619 | Pipelife Greenlife PPR PN10 DN32 | 26.2 | 0.56793 | 0.019122 | 0.022946 |  | 10 | 0.019122 | 0.022946 | 1538.388 | 0.00010316 | 0.017308 | 100000 | 0 | 106.4443 | 106.4443 | 203.5127 | 203.5127 | 185.395 | 185.395 | 187.8249 | 187.8249 | 187.4822 | 187.4822 | 187.5302 | 187.5302 | 187.5234 | 187.5234 | 187.5244 | 187.5244 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243 | 187.5243
5-6 | 3.4 | 2.25 | 0.375 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 1.8193 | 0.27621 | 0.93911 |  | 10 | 0.27621 | 0.93911 | 25532.2175 | 0.00016683 | 0.035598 | 100000 | 0 | 2021.6735 | 2021.6735 | 2802.4649 | 2802.4649 | 2698.2981 | 2698.2981 | 2709.9187 | 2709.9187 | 2708.5943 | 2708.5943 | 2708.7449 | 2708.7449 | 2708.7278 | 2708.7278 | 2708.7297 | 2708.7297 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295 | 2708.7295
6-7 | 3.4 | 5 | 0.55902 | Pipelife Greenlife PPR PN10 DN63 | 51.4 | 0.26941 | 0.0022117 | 0.0075196 |  | 10 | 0.0022117 | 0.0075196 | 176.4556 | 5.2582e-05 | 0.0062988 | 100000 | 0 | 10.2969 | 10.2969 | 24.284 | 24.284 | 21.3348 | 21.3348 | 21.7417 | 21.7417 | 21.6816 | 21.6816 | 21.6904 | 21.6904 | 21.6891 | 21.6891 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893 | 21.6893
7-8 | 3.4 | 7.25 | 0.67315 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 3.2658 | 0.79693 | 2.7096 |  | 10 | 0.79693 | 2.7096 | 82270.4785 | 0.00016683 | 0.035598 | 100000 | 0 | 6514.2812 | 6514.2812 | 7953.6238 | 7953.6238 | 7802.4137 | 7802.4137 | 7816.5789 | 7816.5789 | 7815.2369 | 7815.2369 | 7815.3639 | 7815.3639 | 7815.3519 | 7815.3519 | 7815.3531 | 7815.3531 | 7815.3529 | 7815.3529 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353 | 7815.353
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 3.8355 | 1.0699 | 3.6375 |  | 10 | 1.0699 | 3.6375 | 113476.522 | 0.00016683 | 0.035598 | 100000 | 0 | 8985.2154 | 8985.2154 | 10640.3197 | 10640.3197 | 10478.7112 | 10478.7112 | 10493.0114 | 10493.0114 | 10491.7345 | 10491.7345 | 10491.8484 | 10491.8484 | 10491.8383 | 10491.8383 | 10491.8392 | 10491.8392 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 4.2451 | 1.2893 | 4.3838 |  | 10 | 1.2893 | 4.3838 | 139008.7395 | 0.00016683 | 0.035598 | 100000 | 0 | 11006.8888 | 11006.8888 | 12797.9348 | 12797.9348 | 12631.2688 | 12631.2688 | 12645.4626 | 12645.4626 | 12644.2444 | 12644.2444 | 12644.3488 | 12644.3488 | 12644.3399 | 12644.3399 | 12644.3407 | 12644.3407 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 4.6975 | 1.5542 | 5.2842 |  | 10 | 1.5542 | 5.2842 | 170214.783 | 0.00016683 | 0.035598 | 100000 | 0 | 13477.8231 | 13477.8231 | 15398.898 | 15398.898 | 15228.7838 | 15228.7838 | 15242.7024 | 15242.7024 | 15241.556 | 15241.556 | 15241.6504 | 15241.6504 | 15241.6426 | 15241.6426 | 15241.6433 | 15241.6433 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.0375 | 1.7687 | 6.0135 |  | 10 | 1.7687 | 6.0135 | 195747.0005 | 0.00016683 | 0.035598 | 100000 | 0 | 15499.4965 | 15499.4965 | 17503.7441 | 17503.7441 | 17332.402 | 17332.402 | 17346.0237 | 17346.0237 | 17344.9343 | 17344.9343 | 17345.0214 | 17345.0214 | 17345.0145 | 17345.0145 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.4242 | 2.0286 | 6.8973 |  | 10 | 2.0286 | 6.8973 | 226953.0441 | 0.00016683 | 0.035598 | 100000 | 0 | 17970.4308 | 17970.4308 | 20053.5307 | 20053.5307 | 19882.109 | 19882.109 | 19895.315 | 19895.315 | 19894.2923 | 19894.2923 | 19894.3715 | 19894.3715 | 19894.3653 | 19894.3653 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.7212 | 2.2398 | 8.9593 |  | 10 | 2.2398 | 8.9593 | 252485.2615 | 0.00016683 | 0.035598 | 100000 | 0 | 19992.1042 | 19992.1042 | 22124.0918 | 22124.0918 | 21953.4998 | 21953.4998 | 21966.3386 | 21966.3386 | 21965.3678 | 21965.3678 | 21965.4412 | 21965.4412 | 21965.4356 | 21965.4356 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.9419 | 2.4033 | 3.8452 |  | 10 | 2.4033 | 3.8452 | 272343.6529 | 0.00016683 | 0.035598 | 100000 | 0 | 21564.5169 | 21564.5169 | 23726.1432 | 23726.1432 | 23556.6411 | 23556.6411 | 23569.1839 | 23569.1839 | 23568.2517 | 23568.2517 | 23568.3209 | 23568.3209 | 23568.3158 | 23568.3158 | 23568.3162 | 23568.3162 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161
8-9 | 3.4 | 10 | 0.79057 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 3.8355 | 1.0699 | 3.6375 |  | 10 | 1.0699 | 3.6375 | 113476.522 | 0.00016683 | 0.035598 | 100000 | 0 | 8985.2154 | 8985.2154 | 10640.3197 | 10640.3197 | 10478.7112 | 10478.7112 | 10493.0114 | 10493.0114 | 10491.7345 | 10491.7345 | 10491.8484 | 10491.8484 | 10491.8383 | 10491.8383 | 10491.8392 | 10491.8392 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391 | 10491.8391
9-10 | 3.4 | 12.25 | 0.875 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 4.2451 | 1.2893 | 4.3838 |  | 10 | 1.2893 | 4.3838 | 139008.7395 | 0.00016683 | 0.035598 | 100000 | 0 | 11006.8888 | 11006.8888 | 12797.9348 | 12797.9348 | 12631.2688 | 12631.2688 | 12645.4626 | 12645.4626 | 12644.2444 | 12644.2444 | 12644.3488 | 12644.3488 | 12644.3399 | 12644.3399 | 12644.3407 | 12644.3407 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406 | 12644.3406
10-11 | 3.4 | 15 | 0.96825 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 4.6975 | 1.5542 | 5.2842 |  | 10 | 1.5542 | 5.2842 | 170214.783 | 0.00016683 | 0.035598 | 100000 | 0 | 13477.8231 | 13477.8231 | 15398.898 | 15398.898 | 15228.7838 | 15228.7838 | 15242.7024 | 15242.7024 | 15241.556 | 15241.556 | 15241.6504 | 15241.6504 | 15241.6426 | 15241.6426 | 15241.6433 | 15241.6433 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432 | 15241.6432
11-12 | 3.4 | 17.25 | 1.0383 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.0375 | 1.7687 | 6.0135 |  | 10 | 1.7687 | 6.0135 | 195747.0005 | 0.00016683 | 0.035598 | 100000 | 0 | 15499.4965 | 15499.4965 | 17503.7441 | 17503.7441 | 17332.402 | 17332.402 | 17346.0237 | 17346.0237 | 17344.9343 | 17344.9343 | 17345.0214 | 17345.0214 | 17345.0145 | 17345.0145 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015 | 17345.015
12-13 | 3.4 | 20 | 1.118 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.4242 | 2.0286 | 6.8973 |  | 10 | 2.0286 | 6.8973 | 226953.0441 | 0.00016683 | 0.035598 | 100000 | 0 | 17970.4308 | 17970.4308 | 20053.5307 | 20053.5307 | 19882.109 | 19882.109 | 19895.315 | 19895.315 | 19894.2923 | 19894.2923 | 19894.3715 | 19894.3715 | 19894.3653 | 19894.3653 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658 | 19894.3658
13-14 | 4 | 22.25 | 1.1792 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.7212 | 2.2398 | 8.9593 |  | 10 | 2.2398 | 8.9593 | 252485.2615 | 0.00016683 | 0.035598 | 100000 | 0 | 19992.1042 | 19992.1042 | 22124.0918 | 22124.0918 | 21953.4998 | 21953.4998 | 21966.3386 | 21966.3386 | 21965.3678 | 21965.3678 | 21965.4412 | 21965.4412 | 21965.4356 | 21965.4356 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436 | 21965.436
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.9419 | 2.4033 | 3.8452 |  | 10 | 2.4033 | 3.8452 | 272343.6529 | 0.00016683 | 0.035598 | 100000 | 0 | 21564.5169 | 21564.5169 | 23726.1432 | 23726.1432 | 23556.6411 | 23556.6411 | 23569.1839 | 23569.1839 | 23568.2517 | 23568.2517 | 23568.3209 | 23568.3209 | 23568.3158 | 23568.3158 | 23568.3162 | 23568.3162 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161
14-15 | 1.6 | 24 | 1.2247 | Pipelife Greenlife PPR PN10 DN20 | 16.2 | 5.9419 | 2.4033 | 3.8452 |  | 10 | 2.4033 | 3.8452 | 272343.6529 | 0.00016683 | 0.035598 | 100000 | 0 | 21564.5169 | 21564.5169 | 23726.1432 | 23726.1432 | 23556.6411 | 23556.6411 | 23569.1839 | 23569.1839 | 23568.2517 | 23568.2517 | 23568.3209 | 23568.3209 | 23568.3158 | 23568.3158 | 23568.3162 | 23568.3162 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161 | 23568.3161
[7 empty] | SH = | 43.0487 | m

## Podaci (hidden)
Pipelife Greenlife PPR PN16
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR PN16 DN110 | 79.8 | 110
Pipelife Greenlife PPR PN16 DN16 | 11.6 | 16
Pipelife Greenlife PPR PN16 DN20 | 14.4 | 20
Pipelife Greenlife PPR PN16 DN25 | 18 | 25
Pipelife Greenlife PPR PN16 DN32 | 23.2 | 32
Pipelife Greenlife PPR PN16 DN40 | 29 | 40
Pipelife Greenlife PPR PN16 DN50 | 36.2 | 50
Pipelife Greenlife PPR PN16 DN63 | 45.8 | 63
Pipelife Greenlife PPR PN16 DN75 | 54.4 | 75
Pipelife Greenlife PPR PN16 DN90 | 65.4 | 90
Pipelife Greenlife PPR PN20
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR PN20 DN110 | 73.4 | 110
Pipelife Greenlife PPR PN20 DN16 | 10.6 | 16
Pipelife Greenlife PPR PN20 DN20 | 13.2 | 20
Pipelife Greenlife PPR PN20 DN25 | 16.6 | 25
Pipelife Greenlife PPR PN20 DN32 | 21.2 | 32
Pipelife Greenlife PPR PN20 DN40 | 26.6 | 40
Pipelife Greenlife PPR PN20 DN50 | 33.4 | 50
Pipelife Greenlife PPR PN20 DN63 | 42 | 63
Pipelife Greenlife PPR PN20 DN75 | 50 | 75
Pipelife Greenlife PPR PN20 DN90 | 60 | 90
Pipelife Greenlife PPR GFR PN16
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR GFR PN16 DN110 | 79.8 | 110
Pipelife Greenlife PPR GFR PN16 DN125 | 90.8 | 125
Pipelife Greenlife PPR GFR PN16 DN16 | 11.6 | 16
Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 20
Pipelife Greenlife PPR GFR PN16 DN25 | 18 | 25
Pipelife Greenlife PPR GFR PN16 DN32 | 23.2 | 32
Pipelife Greenlife PPR GFR PN16 DN40 | 29 | 40
Pipelife Greenlife PPR GFR PN16 DN50 | 36.2 | 50
Pipelife Greenlife PPR GFR PN16 DN63 | 45.8 | 63
Pipelife Greenlife PPR GFR PN16 DN75 | 54.4 | 75
Pipelife Greenlife PPR GFR PN16 DN90 | 65.4 | 90
Pipelife Greenlife PPR GFR PN20
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR GFR PN20 DN16 | 10.6 | 16
Pipelife Greenlife PPR GFR PN20 DN20 | 13.2 | 20
Pipelife Greenlife PPR GFR PN20 DN25 | 16.6 | 25
Pipelife Greenlife PPR GFR PN20 DN32 | 21.2 | 32
Pipelife Greenlife PPR GFR PN20 DN40 | 26.6 | 40
Pipelife Greenlife PPR GFR PN20 DN50 | 33.4 | 50
Pipelife Greenlife PPR GFR PN20 DN63 | 42 | 63
Pipelife Greenlife PPR GFR PN20 DN75 | 50 | 75
Pipelife Greenlife PPR GFR PN20 DN90 | 60 | 90
Pipelife Greenlife PPR GFR PN20 DN110 | 73.4 | 110
Pipelife Greenlife PPR GFR PN20 DN125 | 83.4 | 125
Pipelife Radopress PN10
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Radopress PN10 DN16 | 12 | 16
Pipelife Radopress PN10 DN18 | 14 | 18
Pipelife Radopress PN10 DN20 | 16 | 20
Pipelife Radopress PN10 DN26 | 20 | 26
Pipelife Radopress PN10 DN33 | 26 | 33
Pipelife Radopress PN10 DN42 | 33 | 40
Pipelife Radopress PN10 DN54 | 42 | 50
Pipelife Radopress PN10 DN63 | 54 | 63

## Podaci1 (hidden)
Pipelife Greenlife PPR PN16
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR PN16 DN110 | 79.8 | 110
Pipelife Greenlife PPR PN16 DN16 | 11.6 | 16
Pipelife Greenlife PPR PN16 DN20 | 14.4 | 20
Pipelife Greenlife PPR PN16 DN25 | 18 | 25
Pipelife Greenlife PPR PN16 DN32 | 23.2 | 32
Pipelife Greenlife PPR PN16 DN40 | 29 | 40
Pipelife Greenlife PPR PN16 DN50 | 36.2 | 50
Pipelife Greenlife PPR PN16 DN63 | 45.8 | 63
Pipelife Greenlife PPR PN16 DN75 | 54.4 | 75
Pipelife Greenlife PPR PN16 DN90 | 65.4 | 90
Pipelife Greenlife PPR PN20
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR PN20 DN110 | 73.4 | 110
Pipelife Greenlife PPR PN20 DN16 | 10.6 | 16
Pipelife Greenlife PPR PN20 DN20 | 13.2 | 20
Pipelife Greenlife PPR PN20 DN25 | 16.6 | 25
Pipelife Greenlife PPR PN20 DN32 | 21.2 | 32
Pipelife Greenlife PPR PN20 DN40 | 26.6 | 40
Pipelife Greenlife PPR PN20 DN50 | 33.4 | 50
Pipelife Greenlife PPR PN20 DN63 | 42 | 63
Pipelife Greenlife PPR PN20 DN75 | 50 | 75
Pipelife Greenlife PPR PN20 DN90 | 60 | 90
Pipelife Greenlife PPR GFR PN16
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR GFR PN16 DN110 | 79.8 | 110
Pipelife Greenlife PPR GFR PN16 DN125 | 90.8 | 125
Pipelife Greenlife PPR GFR PN16 DN16 | 11.6 | 16
Pipelife Greenlife PPR GFR PN16 DN20 | 14.4 | 20
Pipelife Greenlife PPR GFR PN16 DN25 | 18 | 25
Pipelife Greenlife PPR GFR PN16 DN32 | 23.2 | 32
Pipelife Greenlife PPR GFR PN16 DN40 | 29 | 40
Pipelife Greenlife PPR GFR PN16 DN50 | 36.2 | 50
Pipelife Greenlife PPR GFR PN16 DN63 | 45.8 | 63
Pipelife Greenlife PPR GFR PN16 DN75 | 54.4 | 75
Pipelife Greenlife PPR GFR PN16 DN90 | 65.4 | 90
Pipelife Greenlife PPR GFR PN20
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR GFR PN20 DN16 | 10.6 | 16
Pipelife Greenlife PPR GFR PN20 DN20 | 13.2 | 20
Pipelife Greenlife PPR GFR PN20 DN25 | 16.6 | 25
Pipelife Greenlife PPR GFR PN20 DN32 | 21.2 | 32
Pipelife Greenlife PPR GFR PN20 DN40 | 26.6 | 40
Pipelife Greenlife PPR GFR PN20 DN50 | 33.4 | 50
Pipelife Greenlife PPR GFR PN20 DN63 | 42 | 63
Pipelife Greenlife PPR GFR PN20 DN75 | 50 | 75
Pipelife Greenlife PPR GFR PN20 DN90 | 60 | 90
Pipelife Greenlife PPR GFR PN20 DN110 | 73.4 | 110
Pipelife Greenlife PPR GFR PN20 DN125 | 83.4 | 125
Pipelife Radopress PN10
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Radopress PN10 DN16 | 12 | 16
Pipelife Radopress PN10 DN18 | 14 | 18
Pipelife Radopress PN10 DN20 | 16 | 20
Pipelife Radopress PN10 DN26 | 20 | 26
Pipelife Radopress PN10 DN33 | 26 | 33
Pipelife Radopress PN10 DN42 | 33 | 40
Pipelife Radopress PN10 DN54 | 42 | 50
Pipelife Radopress PN10 DN63 | 54 | 63
Pipelife Greenlife PP-RC PN20
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PP-RC PN20 DN20 | 13.2 | 20 | PP-RC PN20 Ø 20x3.4 | 3.4 | 20 | 13.2
Pipelife Greenlife PP-RC PN20 DN25 | 16.6 | 25 | PP-RC PN20 Ø 25x4.2 | 4.2 | 25 | 16.6
Pipelife Greenlife PP-RC PN20 DN32 | 21.2 | 32 | PP-RC PN20 Ø 32x5.4 | 5.4 | 32 | 21.2
Pipelife Greenlife PP-RC PN20 DN40 | 26.6 | 40 | PP-RC PN20 Ø 40x6.7 | 6.7 | 40 | 26.6
Pipelife Greenlife PP-RC PN20 DN50 | 33.2 | 50 | PP-RC PN20 Ø 50x8.4 | 8.4 | 50 | 33.2
Pipelife Greenlife PP-RC PN20 DN63 | 42 | 63 | PP-RC PN20 Ø 63x10.5 | 10.5 | 63 | 42
Pipelife Greenlife PP-RC PN20 DN75 | 50 | 75 | PP-RC PN20 Ø 75x12.5 | 12.5 | 75 | 50
Pipelife Greenlife PP-RC PN20 DN90 | 60 | 90 | PP-RC PN20 Ø 90x15 | 15 | 90 | 60
Pipelife Greenlife PP-RC PN20 DN110 | 73.2 | 110 | PP-RC PN20 Ø 110x18.4 | 18.4 | 110 | 73.2
Pipelife Carbo PP-RCT PN10
DN / OD k th zidovi: 20k2.8 / 25k3.5 / 32k4.4 / 40k5.5 / 50k6.9 / 63k8.6 / 75k8.4 / 90k10.1 / 110k12.3 / 125k14.0
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Carbo PP-RCT PN10 DN110 PN10 | 85.4 | 110 |  | 12.3 | 110 | 85.4
Pipelife Carbo PP-RCT PN10 DN125 PN10 | 97 | 125 |  | 14 | 125 | 97
Pipelife Carbo PP-RCT PN10 DN20 PN10 | 14.4 | 20 |  | 2.8 | 20 | 14.4
Pipelife Carbo PP-RCT PN10 DN25 PN10 | 18 | 25 |  | 3.5 | 25 | 18
Pipelife Carbo PP-RCT PN10 DN32 PN10 | 23.2 | 32 |  | 4.4 | 32 | 23.2
Pipelife Carbo PP-RCT PN10 DN40 PN10 | 29 | 40 |  | 5.5 | 40 | 29
Pipelife Carbo PP-RCT PN10 DN50 PN10 | 36.2 | 50 |  | 6.9 | 50 | 36.2
Pipelife Carbo PP-RCT PN10 DN63 PN10 | 45.8 | 63 |  | 8.6 | 63 | 45.8
Pipelife Carbo PP-RCT PN10 DN75 PN10 | 56.2 | 75 |  | 9.4 | 75 | 56.2
Pipelife Carbo PP-RCT PN10 DN90 PN10 | 69.8 | 90 |  | 10.1 | 90 | 69.8
Pipelife Unibeta PP-RCT
DN / OD k th zidovi: 16k2.2 / 20k2.3 / 25k2.8 / 32k3.6 / 40k4.5 / 50k5.6 / 63k7.1 / 75k8.4 / 90k10.1 / 110k12.3 / 125k14.0 / 160k14.6 / 200k18,2
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Unibeta PP-RCT PN10 DN110 PN10 | 85.4 | 110 |  | 12.3 | 110 | 85.4
Pipelife Unibeta PP-RCT PN10 DN125 PN10 | 97 | 125 |  | 14 | 125 | 97
Pipelife Unibeta PP-RCT PN10 DN16 PN10 | 11.6 | 16 |  | 2.2 | 16 | 11.6
Pipelife Unibeta PP-RCT PN10 DN160 PN10 | 130.8 | 160 |  | 14.6 | 160 | 130.8
Pipelife Unibeta PP-RCT PN10 DN20 PN10 | 15.4 | 20 |  | 2.3 | 20 | 15.4
Pipelife Unibeta PP-RCT PN10 DN200 PN10 | 163.6 | 200 |  | 18.2 | 200 | 163.6
Pipelife Unibeta PP-RCT PN10 DN25 PN10 | 19.4 | 25 |  | 2.8 | 25 | 19.4
Pipelife Unibeta PP-RCT PN10 DN32 PN10 | 24.8 | 32 |  | 3.6 | 32 | 24.8
Pipelife Unibeta PP-RCT PN10 DN40 PN10 | 31 | 40 |  | 4.5 | 40 | 31
Pipelife Unibeta PP-RCT PN10 DN50 PN10 | 38.8 | 50 |  | 5.6 | 50 | 38.8
Pipelife Unibeta PP-RCT PN10 DN63 PN10 | 48.8 | 63 |  | 7.1 | 63 | 48.8
Pipelife Unibeta PP-RCT PN10 DN75 PN10 | 58.2 | 75 |  | 8.4 | 75 | 58.2
Pipelife Unibeta PP-RCT PN10 DN90 PN10 | 69.8 | 90 |  | 10.1 | 90 | 69.8
C E | V I
ND | DU | DN
(mm) | (mm)
Pipelife Greenlife PPR PN10 DN110 | 90 | 110
Pipelife Greenlife PPR PN10 DN20 | 16.2 | 20
Pipelife Greenlife PPR PN10 DN25 | 20.4 | 25
Pipelife Greenlife PPR PN10 DN32 | 26.2 | 32
Pipelife Greenlife PPR PN10 DN40 | 32.6 | 40
Pipelife Greenlife PPR PN10 DN50 | 40.8 | 50
Pipelife Greenlife PPR PN10 DN63 | 51.4 | 63
Pipelife Greenlife PPR PN10 DN75 | 61.4 | 75
Pipelife Greenlife PPR PN10 DN90 | 73.6 | 90